## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5000 | 4890 | 4128 | 4011 | 872 | 879 | 17.44% | 17.98%
DOAS-1 | KITCHEN | 2900 | 2827 | 0 | 0 | 2900 | 2827 | 100% | 100%
KEF-1 | HOOD 1 | [10 empty] | 1600 | 1620
KEF-2 | HOOD 2 | [10 empty] | 775 | 792
KEF-3 | HOOD 2 | [10 empty] | 525 | 552
EF-1 | RESTROOM | [12 empty] | 75 | 181
EF-2 | RESTROOM | [12 empty] | 75 | 107
TOTALS |  | 7900 | 7717 | 4128 | 4011 | 3772 | 3706 |  |  | 0 | 0 | 2900 | 2964 | 150 | 288
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3772 | 3706 |  | FRONT |  | 0.0182 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3050 | 3252 |  | SIDE |  | 0.0172 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 722 | 454 |  | REAR |  | 0.0196 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.018333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0