## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
DOAS-1 | KITCHEN | 2000 | 2017 | 0 | 0 | 2000 | 2017 | 100% | 100%
FCU-1 | DINING | 1300 | 1425 | 1300 | 1425 | 0 | 0 | 0% | 0%
FCU-2 | DINING | 1300 | 1425 | 1300 | 1425 | 0 | 0 | 0% | 0%
FCU-3 | KITCHEN | 1300 | 1231 | 1300 | 1231 | 0 | 0 | 0% | 0%
FCU-4 | KITCHEN | 1300 | 1231 | 1300 | 1231 | 0 | 0 | 0% | 0%
FCU-5 | BOH | 850 | 482 | 850 | 482 | 0 | 0 | 0% | 0%
FCU-6 | OFFICE |  |  |  |  | 50 | 21 | #DIV/0! | #DIV/0!
KEF-1 | KITCHEN HD | [10 empty] | 1450 | 1469
EF-1 | RESTROOM | [12 empty] | 150 | 157
TOTALS |  | 8050 | 7811 | 6050 | 5794 | 2050 | 2038 |  |  | 0 | 0 | 1450 | 1469 | 150 | 157
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2050 | 2038 |  | FRONT |  | 0.0017 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1600 | 1626 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 450 | 412 |  | REAR |  | 0.0021 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0019 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2000
TOTAL KITCHEN EXHAUST |  | 1450
NET AIRFLOW |  | 550 | 0
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0