## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | DINING | 6750 | 6427 | 4770 | 4337 | 1980 | 2090 | 29.33% | 32.52%
RTU-2 | KITCHEN | 6150 | 6199 | 4655 | 4644 | 1495 | 1555 | 24.31% | 25.08%
PRV 2 | GRIDDLE HOOD | [10 empty] | 1500 | 1542
PRV 3 | FRYER HOOD | [10 empty] | 1500 | 1506
PRV 1 | RESTROOM | [12 empty] | 400 | 403
EF1-A | MOP ROOM | [12 empty] | 75 | 71
TOTALS |  | 12900 | 12626 | 9425 | 8981 | 3475 | 3645 |  |  | 0 | 0 | 3000 | 3048 | 475 | 474
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3475 | 3645 |  | FRONT |  | 0.0075 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3475 | 3522 |  | SIDE |  | 0.0101 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 123 |  | REAR |  | N/A | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0088 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
UNABLE TO RECORD ACCURATE BUILDING PRESSURE READING AT BACK DOOR DUE TO SIGNIFICANT WIND HITTING THIS DOORWAY.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0