## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | RETAIL | 3400 | 3495 | 2900 | 2977 | 500 | 518 | 14.71% | 14.82%
RTU-2 | FOOD SERVICE | 5000 | 5139 | 4350 | 4521 | 650 | 618 | 13% | 12.03%
RTU-3 | RETAIL | 3000 | 3098 | 2700 | 2784 | 300 | 314 | 10% | 10.14%
EF-1 | FOOD SERVICE | [12 empty] | 850 | 880
EF-2 | WATER SERVICE | [12 empty] | 60 | 58
TOTALS |  | 11400 | 11732 | 9950 | 10282 | 1450 | 1450 |  |  | 0 | 0 | 0 | 0 | 910 | 938
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1450 | 1450 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 910 | 938 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 540 | 512 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0