## SUMMARY (2)
CORE
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FOOD SERVICE | 5000 | 5016 | 4060 | 4071 | 940 | 945 | 18.8% | 18.84%
RTU-2 | RETAIL | 4000 | 4016 | 3300 | 3327 | 700 | 689 | 17.5% | 17.16%
RTU-3 | FOH | 2000 |  | 1600 |  | 400 |  | 20% | #DIV/0!
RTU-4 | FOH | 2000 | 2020 | 1600 | 1617 | 400 | 403 | 20% | 19.95%
EF-1 | RESTROOMS | [12 empty] | 1500 | 0
EF-2 | KITCHEN | [12 empty] | 400 | 0
EF-3 | TRASH | [12 empty] | 200 | 0
TOTALS |  | 13000 | 11052 | 10560 | 9015 | 2440 | 2037 |  |  | 0 | 0 | 0 | 0 | 2100 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2440 | 2037 |  | FRONT |  | 0.052 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2100 | 0 |  | SIDE |  | 0.053 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 340 | 2037 |  | REAR |  | 0.054 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.053 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
Unable to establish totals for RTU 3
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0