## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 8737 | 7125 | 6552 | 2375 | 2185 | 25% | 25.01%
AC-2 | DRIVE THRU | 3400 | 3244 | 2550 | 2425 | 850 | 819 | 25% | 25.25%
AC-3 | DINING | 4100 | 4248 | 3100 | 3317 | 1000 | 931 | 24.39% | 21.92%
AC-4 | DINING | 3800 | 3958 | 2850 | 2990 | 950 | 968 | 25% | 24.46%
AHU1 | KIOSK |  |  |  |  | 50 | 45
AHU2 | KIOSK | 1250 | 1305 |  |  | 200 | 182
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 2610 | 2679
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1471
EF-3 | RESTROOM | [12 empty] | 150 | 156
EF4 | RESTROOM | [12 empty] | 150 | 104
TOTALS |  | 22050 | 21492 | 15625 | 15284 | 5425 | 5130 |  |  | 0 | 0 | 4012 | 4150 | 150 | 156
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5425 | 5130 |  | FRONT |  | 0.008 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4162 | 4306 |  | SIDE |  | 0.007 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1263 | 824 |  | REAR |  | 0.006 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.007 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390