## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3350 | 3246 | 0 | 0 | 3350 | 3246 | 100% | 100%
RTU-2 | KITCHEN | 3350 | 3347 | 0 | 0 | 3350 | 3347 | 100% | 100%
RTU-3 | KITCHEN | 3350 | 3229 | 0 | 0 | 3350 | 3229 | 100% | 100%
RTU-4 | DINING | 3000 | 3016 | 1650 | 1236 | 1350 | 1780 | 45% | 59.02%
RTU-5 | DINING | 3000 | 2975 | 1650 | 1163 | 1350 | 1812 | 45% | 60.91%
EF-1 | KITCHEN HD 1 | [10 empty] | 3900 | 3912
EF-2 | KITCHEN HD 2 | [10 empty] | 1575 | 1572
EF-3 | KITCHEN HD 3 | [10 empty] | 2100 | 2082
EF-4 | KITCHEN HD 4 | [10 empty] | 2000 | 2024
EF-5 | KITCHEN HD 5&6 | [10 empty] | 1900 | 1877
EF-6 | RESTROOM | [12 empty] | 750 | 763
TOTALS |  | 16050 | 15813 | 3300 | 2399 | 12750 | 13414 |  |  | 0 | 0 | 11475 | 11467 | 750 | 763
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 12750 | 13414 |  | FRONT |  | -0.002 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 12225 | 12230 |  | SIDE |  | 0.017 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 525 | 1184 |  | REAR |  | 0.016 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.010333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390