## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | RETAIL | 3400 | 3426 | 2855 | 2887 | 545 | 539 | 16.03% | 15.73%
RTU-2 | FOOD SERVICE | 4000 | 3968 | 3350 | 3308 | 650 | 660 | 16.25% | 16.63%
RTU-3 | RETAIL | 2000 | 1966 | 1695 | 1656 | 305 | 310 | 15.25% | 15.77%
EF-1 | RESTROOM | [12 empty] | 300 | 312
EF-2 | WASHROOM | [12 empty] | 900 | 893
EF-3 | ELECTRCIAL RM | [12 empty] | 60 | 62
TOTALS |  | 9400 | 9360 | 7900 | 7851 | 1500 | 1509 |  |  | 0 | 0 | 0 | 0 | 1260 | 1267
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1500 | 1509 |  | FRONT |  | 0.0016 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1260 | 1267 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 240 | 242 |  | REAR |  | 0.0042 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0029 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0