## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8500 | 8579 | 6500 | 6508 | 2000 | 2071 | 23.53% | 24.14%
AC-2 | DINNING B | 2830 | 2833 | 2080 | 2032 | 750 | 801 | 26.5% | 28.27%
AC-3 | DRIVE THRU | 4000 | 4052 | 3000 | 3079 | 1000 | 973 | 25% | 24.01%
AC-4 | DINNING A | 2765 | 2826 | 2165 | 2209 | 600 | 617 | 21.7% | 21.83%
AC-5 | PLAY AREA | 1800 | 1864 | 1500 | 1559 | 300 | 305 | 16.67% | 16.36%
AC-6 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1951
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1434
EF-3 | RESTROOM | [12 empty] | 475 | 481
TOTALS |  | 19895 | 20154 | 15245 | 15387 | 4650 | 4767 |  |  | 0 | 0 | 3315 | 3385 | 475 | 481
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4767 |  | FRONT |  | 0.0076 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3790 | 3866 |  | SIDE |  | 0.0057 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 860 | 901 |  | REAR |  | 0.0083 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0072 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390