## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | DINING | 6150 | 6298 | 4250 | 4357 | 1900 | 1941 | 30.89% | 30.82%
RTU-2 | KITCHEN | 6150 | 6419 | 4250 | 4461 | 1900 | 1958 | 30.89% | 30.5%
PRV 2 | HOOD1 | [10 empty] | 1500 | 1512
PRV 3 | HOOD 2 | [10 empty] | 1500 | 1522
EF-1A | DISHHOOD | [10 empty] | 350 | 362
PRV 1 | RESTROOMS | [12 empty] | 375 | 354
EF1 | MOPROOM | [12 empty] | 75 | 80
TOTALS |  | 12300 | 12717 | 8500 | 8818 | 3800 | 3899 |  |  | 0 | 0 | 3350 | 3396 | 450 | 434
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3800 | 3899 |  | FRONT |  | 0.0076 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3800 | 3830 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 69 |  | REAR |  | 0.0084 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.008 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0