## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3300 | 3310 | 0 | 0 | 3300 | 3310 | 100% | 100%
RTU-2 | DINING | 2800 | 2686 | 550 | 478 | 2250 | 2208 | 80.36% | 82.2%
RTU-3 | KITCHEN/BOH | 2800 | 2790 | 550 | 509 | 2250 | 2281 | 80.36% | 81.76%
EF-1 | KITCHEN HD 1 | [10 empty] | 1500 | 1558
EF-2 | KITCHEN HD 2 | [10 empty] | 1400 | 1396
EF-3 | KITCHEN HD 3 | [10 empty] | 2090 | 2172
EF-4 | KITCHEN HD 4 | [10 empty] | 2090 | 2111
EF-5 | RESTROOM | [12 empty] | 200 | 212
TOTALS |  | 8900 | 8786 | 1100 | 987 | 7800 | 7799 |  |  | 0 | 0 | 7080 | 7237 | 200 | 212
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 7800 | 7799 |  | FRONT |  | 0.011 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 7280 | 7449 |  | SIDE |  | 0.01 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 520 | 350 |  | REAR |  | 0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.008 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390