## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 7361 | 6750 | 7361 | 2000 | 0 | 22.86% | 0%
AC-2 | DINNING A | 3150 | 2685 | 2550 | 2118 | 600 | 567 | 19.05% | 21.12%
AC-3 | N. DINNING B | 5250 | 4795 | 4250 | 3723 | 1000 | 1072 | 19.05% | 22.36%
AC-4 | S. DINNING B | 2890 | 2848 | 2390 | 2311 | 500 | 537 | 17.3% | 18.86%
AC-5 | DINNING B | 1800 | 1787 | 1500 | 1499 | 300 | 288 | 16.67% | 16.12%
EF-2 | HD 3 | [10 empty] | 701 | 671
EF-3 | RESTROOMS | [12 empty] | 500 | 512
EF-4 | HD1 -L/R | [10 empty] | 1913 | 1796
EF-5 | HD 2 | [10 empty] | 701 | 702
TOTALS |  | 21840 | 19476 | 17440 | 17012 | 4400 | 2464 |  |  | 0 | 0 | 3315 | 3169 | 500 | 512
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 4400 | 2464 |  | FRONT |  | -0.0012 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3815 | 3681 |  | SIDE |  | -0.025 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 585 | -1217 |  | REAR |  | -0.016 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.014067 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390