## Sheet1
Summary
What was found initially: | MAU is not delivering correct amount of CFM, delivering 66% of what's required. Hood 4 not exhausting correct amount of CFM, exhausting 62% of what's required. RTU-1 and RTU-3 OA found at 0% open. PSPs for Hoods 1-4 are clogged.
Changes made: | Lowered Fan Speed for Hood-1 Raised Fan Speed for Hood-4 Readjusted OA for RTU-1, RTU-2, and RTU-3
Air balancing & performance related issues that need to be resolved: | PSPs for Hoods are clogged, recommend cleaning.
Air Balance Schedule
AIR GOING IN (+) | Target | Initial | Final
RTU-1 OA | 700 | 0 | 723
RTU-2 OA | 600 | 1207 | 954 |  |  |  | Air Going In |  | Air Going out
RTU-3 OA | 1400 | 0 | 1495 |  |  |  | 5789 |  | 5253
RTU-4 OA | 0
RTU-5 OA | 0
RTU-6 OA | 0
MUA-1 | 4260 | 2801 | 2617
MUA-2 | 0
MUA-3 | 0
AIR GOING OUT (-)
EF-1 | 1050 | 1196 | 1009
EF-2 | 1575 | 1674 | 1674 |  |  |  |  | Air Going In - Air Going out =
EF-3 | 1462.5 | 1481 | 1481 |  |  |  |  | 536
EF-4 | 1237.5 | 765 | 1089 | [10 empty] | Building Pressures:
EF-5 | 0 | [6 empty] | Building Pressure Average: | [5 empty] | Front | -0.04
EF-6 | 0 | [6 empty] | -0.04 | [5 empty] | Side | -0.04
EF-7 | 0 | [12 empty] | Back | -0.04
RR Exhaust (Total) | 300 | 502
NET AIRFLOW (TARGET +200 CFM)
| 1335 | -1610 | 536
Target Airflow Calculations
Unit | Tonnage | Target OA | OA %
RTU-1 | 17.5 | 700 | 10%
RTU-2 | 15 | 600 | 10%
RTU-3 | 17.5 | 1400 | 20%
RTU-4 |  | 0 | N/A
RTU-5 |  | 0 | N/A
RTU-6 |  | 0 | N/A
Hoods | Served by | Served by | Type | Length (in) | Width (in) | MUA Type | Equipment 1 | Equipment 2 | Equipment 3 | CFM/ft1 | CFM/ft 2 | CFM/ft3 | CFM/ft Target | Target Exhaust | Target MUA
Hood 1 | EF-1 | MUA-1 | Type I | 84 | 54 | PSP | Ovens |  |  | 150 | NOT FOUND | NOT FOUND | 150 | 1050 | 840
Hood 2 | EF-2 | MUA-1 | Type I | 84 | 60 | PSP | Ovens | Fryers |  | 150 | 225 | NOT FOUND | 225 | 1575 | 1260
Hood 3 | EF-3 | MUA-1 | Type I | 78 | 54 | PSP | Griddle - Flat Top |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 1462.5 | 1170
Hood 4 | EF-4 | MUA-1 | Type I | 66 | 33.5 | PSP | Fryers |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 1237.5 | 990
Hood 5 | [9 empty] | NOT FOUND | NOT FOUND | NOT FOUND | 0 | 0 | #N/A
Restrooms | # of Toilets/Urinals | Target CFM
RR Exhaust (Total) | 4 | 300

## Kitchen Equipment
Equipment | CFM/ft
Char Grill | 275
Fryers | 225
Griddle - Flat Top | 225
Ovens | 150
Salamander | 275
Range | 200

## MUA Type
PSP | 0.8
Short Cycle | 0.5
Back Return | 0.5

## Sheet2
EF-1 | MUA-1 | Type I
EF-2 | MUA-2
EF-3 | MUA-3
EF-4
EF-5
EF-6
EF-7