## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4000 | 3922 | 3500 | 3414 | 500 | 508 | 12.5% | 12.95%
RTU-2 | DINING | 4000 | 4106 | 3000 | 3113 | 1000 | 993 | 25% | 24.18%
EF-1 | COOK LINE | [10 empty] | 2869 | 2843
EF-2 | BATHROOM | [12 empty] | 150 | 151
MAU1 | HOOD | [8 empty] | 1600 | 1587
TOTALS |  | 8000 | 8028 | 6500 | 6527 | 1500 | 1501 |  |  | 1600 | 1587 | 2869 | 2843 | 150 | 151
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3100 | 3088 |  | FRONT |  | 0.0045 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3019 | 2994 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 81 | 94 |  | REAR |  | 0.0015 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.003 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0