## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8000 | 7223 | 6000 | 5158 | 2000 | 2065 | 25% | 28.59%
AC-2 | SIDE DINING | 2830 | 3062 | 2080 | 2260 | 750 | 802 | 26.5% | 26.19%
AC-3 | MAIN DINING | 5000 | 5349 | 3645 | 3926 | 1355 | 1423 | 27.1% | 26.6%
AC-4 | FRONT DINING | 1800 | 1863 | 1500 | 1536 | 300 | 327 | 16.67% | 17.55%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 2027
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1364
EF-3 | RESTROOM | [12 empty] | 400 | 390
TOTALS |  | 17630 | 17497 | 13225 | 12880 | 4405 | 4617 |  |  | 0 | 0 | 3314 | 3391 | 400 | 390
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4405 | 4617 |  | FRONT |  | 0.001 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3714 | 3781 |  | SIDE |  | 0.004 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 691 | 836 |  | REAR |  | 0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.002 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390