## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FCU-1 | BOH | 1900 | 1732 | 1610 | 1732 | 290 |  | 15.26% | 0%
FCU-2 | SALES | 1400 | 1516 | 1095 | 1516 | 305 |  | 21.79% | 0%
FCU-3 | SALES | 1400 | 1542 | 1095 | 1542 | 305 |  | 21.79% | 0%
FCU-4 | SALES | 1400 | 1176 | 1095 | 1176 | 305 |  | 21.79% | 0%
FCU-5 | SOLAR ZONE | 1200 | 870 | 1200 | 870 | 0 |  | 0% | 0%
SF-1 | FCU1-4 | [8 empty] | 600 | 2021
EF-1 | RESTROOM | [12 empty] | 200 | 98
TOTALS |  | 7300 | 6836 | 6095 | 6836 | 1205 | 0 |  |  | 600 | 2021 | 0 | 0 | 200 | 98
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1805 | 2021 |  | FRONT |  | 0 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 200 | 98 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1605 | 1923 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0