## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 9027 | 7000 | 7318 | 1750 | 1709 | 20% | 18.93%
AC-2 | DINING A | 3000 | 3121 | 2400 | 2486 | 600 | 635 | 20% | 20.35%
AC-3 | E. DINING B | 4920 | 4220 | 3820 | 3219 | 1100 | 1001 | 22.36% | 23.72%
AC-4 | W. DINING B | 2000 | 1805 | 1600 | 1399 | 400 | 406 | 20% | 22.49%
AC-5 | MULTI-PURPOSE | 1100 | 1097 | 900 | 889 | 200 | 208 | 18.18% | 18.96%
EF-1 | HD1 L&R | [10 empty] | 1912 | 1767
EF-2 | HD2 | [10 empty] | 701 | 658
EF-3 | HD3 | [10 empty] | 390 | 397
EF-4 | RESTROOMS | [12 empty] | 530 | 357
TOTALS |  | 19770 | 19270 | 15720 | 15311 | 4050 | 3959 |  |  | 0 | 0 | 3003 | 2822 | 530 | 357
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4050 | 3959 |  | FRONT |  | 0.016 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3533 | 3179 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 517 | 780 |  | REAR |  | 0.016 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.016 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0