## Sheet1
Summary
What was found initially: | Initially found building negative with AVG: -0.0203". All fans are functional. Outside air for RTU#1 was found high as manual damper was mostly open, while RTU#3 economizer was fully shut on the prodigy board. Hoods were found to be functional, however, many of the filters do not cover the gaps in the hood.
Changes made: | RTUs OA balanced at 20% of design airflow
Air balancing & performance related issues that need to be resolved: | EF#2 and EF#3 sheaves are seized. Unable to reduce airflow within design tolerance, sheaves should be replaced and balanced. EF#4 is at minimum setting, however, it is at 129% of design airflow. Sheave needs to be replaced with appropriate size to be balanced within design airflow. MUA has low airflow, blower wheel needs to be cleaned in order to increase airflow within design tolerance.
Air Balance Schedule
AIR GOING IN (+) | Target | Initial | Final
RTU-1 OA | 1100 | 2771 | 1233
RTU-2 OA | 1100 | 845 | 1247 |  |  |  | Air Going In |  | Air Going out
RTU-3 OA | 1200 | 0 | 1445 |  |  |  | 4276 |  | 5109
RTU-4 OA | 0
RTU-5 OA | 0
RTU-6 OA | 0
MUA-1 | 1165.625 | 351 | 351
MUA-2 | 0
MUA-3 | 0
AIR GOING OUT (-)
EF-1 | 1050 | 907 | 907
EF-2 | 700 | 1298 | 1298 |  |  |  |  | Air Going In - Air Going out =
EF-3 | 581.25 | 789 | 789 |  |  |  |  | -833
EF-4 | 637.5 | 829 | 829
EF-5 | 0 | [6 empty] | Building Pressure Average:
EF-6 | 800 | 814 | 814 |  |  |  |  | -0.018
EF-7 | 0
RR Exhaust (Total) | 600 | 472 | 472
NET AIRFLOW (TARGET +200 CFM)
| 196.875 | -1142 | -833
Target Airflow Calculations
Unit | Tonnage | Target OA | OA %
RTU-1 | 15 | 1200 | 20%
RTU-2 | 15 | 1200 | 20%
RTU-3 | 17.5 | 1400 | 20%
RTU-4 |  | 0 | N/A
RTU-5 |  | 0 | N/A
RTU-6 |  | 0 | N/A
Hoods | Served by | Served by | Type | Length (in) | Width (in) | MUA Type | Equipment 1 | Equipment 2 | Equipment 3 | CFM/ft1 | CFM/ft 2 | CFM/ft3 | CFM/ft Target | Target Exhaust | Target MUA
Hood 1 | EF-1 | MUA-1 | Type I | 56 | 70 | Short Cycle | Griddle - Flat Top |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 1050 | 525
Hood 2 | EF-2 | MUA-1 | Type I | 56 | 90 | Short Cycle | Ovens |  |  | 150 | NOT FOUND | NOT FOUND | 150 | 700 | 350
Hood 3 | EF-3 | MUA-1 | Type I | 31 | 84 | Short Cycle | Fryers |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 581.25 | 290.625
Hood 4 | EF-4 |  | Type I | 51 | 66 |  | Ovens |  |  | 150 | NOT FOUND | NOT FOUND | 150 | 637.5 | #N/A
Hood 5 | [9 empty] | NOT FOUND | NOT FOUND | NOT FOUND | 0 | 0 | #N/A
Restrooms | # of Toilets/Urinals | Target CFM
RR Exhaust (Total) | 8 | 600

## Kitchen Equipment
Equipment | CFM/ft
Char Grill | 275
Fryers | 225
Griddle - Flat Top | 225
Ovens | 150
Salamander | 275
Range | 200

## MUA Type
PSP | 0.8
Short Cycle | 0.5
Back Return | 0.5

## Sheet2
EF-1 | MUA-1 | Type I
EF-2 | MUA-2
EF-3 | MUA-3
EF-4
EF-5
EF-6
EF-7