## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | STORAGE | 1400 | 1443 | 1250 | 1286 | 150 | 157 | 10.71% | 10.88%
RTU-2 | WEST SALES | 2800 | 2953 | 2150 | 2312 | 650 | 641 | 23.21% | 21.71%
RTU-3 | EAST SALES | 2800 | 2987 | 2150 | 2326 | 650 | 661 | 23.21% | 22.13%
RTU-4 | SOUTH SALES | 3500 | 3728 | 2725 | 2964 | 775 | 764 | 22.14% | 20.49%
EF-1 | RESTROOM | [12 empty] | 75 | 78
EF-2 | RESTROOM | [12 empty] | 75 | 77
TOTALS |  | 10500 | 11111 | 8275 | 8888 | 2225 | 2223 |  |  | 0 | 0 | 0 | 0 | 150 | 155
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2225 | 2223 |  | FRONT |  | 0.023 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 150 | 155 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 2075 | 2068 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | 0.023 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0