## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3358 | 3150 | 3092 | 250 | 266 | 7.353% | 7.921%
RTU-2 | DINING | 4000 | 4387 | 3325 | 3704 | 675 | 683 | 16.88% | 15.57%
MUA-1 | KITCHEN HD | [8 empty] | 1854 | 1895
KEF-1 | KITCHEN HD | [10 empty] | 2317 | 2163
EF-2 | RESTROOMS | [12 empty] | 250 | 244
TOTALS |  | 7400 | 7745 | 6475 | 6796 | 925 | 949 |  |  | 1854 | 1895 | 2317 | 2163 | 250 | 244
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2779 | 2844 |  | FRONT |  | 0.0025 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2567 | 2407 |  | SIDE |  | 0.0031 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 212 | 437 |  | REAR |  | 0.0043 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0033 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0