## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 2720 | 2734 | 1960 | 1957 | 760 | 777 | 27.94% | 28.42%
RTU-2 | KITCHEN | 2820 | 2793 | 2455 | 2398 | 365 | 395 | 12.94% | 14.14%
EF-1 | KITCHEN | [12 empty] | 750 | 754
EF-2 | RESTROOMS | [12 empty] | 150 | 147
TOTALS |  | 5540 | 5527 | 4415 | 4355 | 1125 | 1172 |  |  | 0 | 0 | 0 | 0 | 900 | 901
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1125 | 1172 |  | FRONT |  | -0.04 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 900 | 901 |  | SIDE |  | -0.02 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 225 | 271 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | -0.03 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
Wind blowing on sides of building causing high pressure zones at exterior.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0