## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | BOH | 300 | 273 | 290 | 258 | 10 | 15 | 3.333% | 5.495%
AC-2 | BOH | 1300 | 963 | 1155 | 828 | 145 | 135 | 11.15% | 14.02%
AC-3 | BOH | 1300 | 862 | 1155 | 732 | 145 | 130 | 11.15% | 15.08%
AC-4 | DINING | 1300 | 1100* | 950 | #VALUE! | 350 | 334 | 26.92% | #VALUE!
AC-5 | DINING | 1200 | 1364 | 850 | 1015 | 350 | 349 | 29.17% | 25.59%
OAF-1 | AC UNITS |  |  |  |  | 1000 | 960
GX-1 | BOH | [12 empty] | 750 | 775
TX-1 | RESTROOM | [12 empty] | 150 | 170
TOTALS |  | 5400 | 3462 | 4400 | #VALUE! | 2000 | 1923 |  |  | 0 | 0 | 0 | 0 | 900 | 945
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2000 | 1923 |  | FRONT | [10 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 900 | 945 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1100 | 978 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.006 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0