## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | BOH | 300 | 273 | 290 | 262 | 10 | 11 | 3.333% | 4.029%
AC-2 | BOH | 1342 | 963 | 1197 | 828 | 145 | 135 | 10.8% | 14.02%
AC-3 | BOH | 1342 | 862 | 1197 | 723 | 145 | 139 | 10.8% | 16.13%
AC-4 | DINING | 1342 | 1246 | 992 | 912 | 350 | 334 | 26.08% | 26.81%
AC-5 | DINING | 1412 | 1364 | 1062 | 1015 | 350 | 349 | 24.79% | 25.59%
OAF-1 | AC UNITS |  |  |  |  | 1000 | 968
GX-1 | BOH | [12 empty] | 750 | 799
TX-1 | RESTROOM | [12 empty] | 150 | 147
TOTALS |  | 5738 | 4708 | 4738 | 3740 | 1000 | 968 |  |  | 0 | 0 | 0 | 0 | 900 | 946
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1000 | 968 |  | FRONT |  | 0.004 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 900 | 946 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 22 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0