## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8000 | 7918 | 6200 | 6155 | 1800 | 1763 | 22.5% | 22.27%
AC-2 | SIDE DINNING | 2830 | 2801 | 2080 | 2041 | 750 | 760 | 26.5% | 27.13%
AC-3 | DRIVE THRU | 4000 | 4117 | 3000 | 3088 | 1000 | 1029 | 25% | 24.99%
AC-4 | MAIN DINNING | 2765 | 2629 | 2165 | 2035 | 600 | 594 | 21.7% | 22.59%
AC-5 | PLAY AREA | 1800 | 1844 | 1500 | 1533 | 300 | 311 | 16.67% | 16.87%
AHU-1 | BOH | 625 | 695 | 600 | 695 | 25 | 0 | 4% | 0%
EF-1 | HD 1 | [10 empty] | 1913 | 1880
EF-2 | HD 2 & 3 | [10 empty] | 1402 | 1354
EF-3 | RESTROOM | [12 empty] | 400 | 408
EF-4 | HD 3
EF-5
TOTALS |  | 20020 | 20004 | 15545 | 15547 | 4475 | 4457 |  |  | 0 | 0 | 3315 | 3234 | 400 | 408
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4475 | 4457 |  | FRONT |  | 0.0187 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3715 | 3642 |  | SIDE |  | 0.0179 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 760 | 815 |  | REAR |  | 0.0152 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.017267 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390