## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3507 | 2450 | 2597 | 950 | 910 | 27.94% | 25.95%
RTU-2 | DINING | 4000 | 3867 | 2850 | 2780 | 1150 | 1087 | 28.75% | 28.11%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 2096
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3078
EF-2 | RESTROOM | [12 empty] | 150 | 159
EF-3 | [13 empty] | 600 | 598
TOTALS |  | 7400 | 7374 | 5300 | 5377 | 2100 | 1997 |  |  | 1950 | 2096 | 3200 | 3078 | 750 | 159
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4050 | 4093 |  | FRONT |  | -0.02 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 3950 | 3237 |  | SIDE |  | -0.04 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 100 | 856 |  | REAR |  | -0.03 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.03 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD-1 | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250
HD-2 | CAPTIVE-AIRE | [11 empty] | 600 |  | -600