## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
DOAS-1 | KITCHEN | 1500 | 1625 | 0 | 1628 | 1500 | 1628 | 100% | 100.2%
DOAS-2 | KITCHEN | 2200 | 2066 | 0 | 0 | 2200 | 2066 | 100% | 100%
DOAS-3 | COOKING | 3000 | 2701 | 0 | 0 | 3000 | 2701 | 100% | 100%
AHU-1 | TASTING ROOM | 1750 | 1649 | 1490 | 1400 | 260 | 249 | 14.86% | 15.1%
EF-1 | HD1 SMOKER | [10 empty] | 1500 | 1489
EF-2 | HD2 OVEN | [10 empty] | 2200 | 2229
EF-3 | HD3 FRYER | [10 empty] | 2738 | 2808
EF-4 | RESTROOMS | [12 empty] | 75 | 31
TOTALS |  | 8450 | 8041 | 1490 | 3028 | 6960 | 6644 |  |  | 0 | 0 | 6438 | 6526 | 75 | 31
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 6960 | 6644 |  | FRONT |  | 0.003 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 6513 | 6557 |  | SIDE |  | 0.006 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 447 | 87 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0043333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0