## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4850 | 4708 | 3850 | 3665 | 1000 | 1043 | 20.62% | 22.15%
RTU-2 | KITCHEN | 3000 | 3086 | 2700 | 2758 | 300 | 328 | 10% | 10.63%
MUA-1 | COOKLINE | [8 empty] | 1980 | 1988
KEF-1 | HOOD 1 | [10 empty] | 1600 | 1620
KEF-2 | HOOD 2 | [10 empty] | 875 | 831
KEF-4 | HOOD 3 | [10 empty] | 525 | 562
EF-1 | WOMENS RESTROOM | [12 empty] | 75 | 71
EF-2 | MENS RESTROOM | [12 empty] | 150 | 158
TOTALS |  | 7850 | 7794 | 6550 | 6423 | 1300 | 1371 |  |  | 1980 | 1988 | 3000 | 3013 | 225 | 229
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3280 | 3359 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3225 | 3242 |  | SIDE |  | 0.0051 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 55 | 117 |  | REAR |  | 0.0007 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0036 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0