Project: Texas Workforce Commission Summary

PROJECT SUMMARY

Equipment to be tested, adjusted, and balanced, was 4 exhaust fans (EF), and 6 supply diffusers.

EF-3 serving the exhaust grille in breakroom 108 is not operational due to a seized motor. The breakroom has no exhaust currently.

EF-4 serving restrooms 106 and 107 was adjusted to +/- 10% of the engineer’s specified design CFM. Dampers on the individual grilles were then adjusted to bring them into tolerance of the specified CFM.

EF-5&6 serving private restrooms 102 and 103 are ceiling mounted. They were first measured in high speed and determined to be too high in flow. After re-wiring them to low speed, they were re-measured and calculated as being 174% and 111% of design airflow respectively. This is not anticipated to create an issue.

All supply grilles were tested, then using the provided volume dampers, brought down to the engineer’s specified CFM. No issues associated with supply grilles are noted.