## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
DOAS-1 | SALES OA | 2645 | 2704 | 0 | 0 | 2645 | 2704 | 100% | 100%
DOAS-2 | SALES OA | 2645 | 0 | 0 | 0 | 2645 | 0 | 100% | #DIV/0!
RTU-1 | SALES | 5000 | 0 | 5000 | 0 | 0 | 0 | 0% | #DIV/0!
RTU-2 | SALES | 5000 | 5321 | 5000 | 5321 | 0 | 0 | 0% | 0%
RTU-3 | SALES | 5000 | 5017 | 5000 | 5017 | 0 | 0 | 0% | 0%
RTU-4 | SALES | 5000 | 5111 | 5000 | 5111 | 0 | 0 | 0% | 0%
RTU-5 | SALES | 5000 | 4991 | 5000 | 4991 | 0 | 0 | 0% | 0%
RTU-6 | SALES | 5000 | 5313 | 5000 | 5313 | 0 | 0 | 0% | 0%
RTU-7 | SALES | 5000 | 5330 | 5000 | 5330 | 0 | 0 | 0% | 0%
RTU-8 | SALES | 5000 | 5245 | 5000 | 5245 | 0 | 0 | 0% | 0%
RTU-9 | SALES | 5000 | 5205 | 5000 | 5205 | 0 | 0 | 0% | 0%
RTU-10 | SALES | 5000 | 5067 | 5000 | 5067 | 0 | 0 | 0% | 0%
RTU-11 | PHARM. | 4000 | 3930 | 3650 | 3607 | 350 | 323 | 8.75% | 8.219%
RTU-13 | TLC | 1200 | 1242 | 1000 | 1040 | 200 | 202 | 16.67% | 16.26%
RTU-14 | VESTIBULES | 5000 | 5259 | 4725 | 4967 | 275 | 292 | 5.5% | 5.552%
RTU-15 | SEATING | 2400 | 2410 | 1800 | 1793 | 600 | 617 | 25% | 25.6%
RTU-16 | DELI | 4000 | 3678 | 3300 | 3026 | 700 | 652 | 17.5% | 17.73%
RTU-17 | BAKERY | 2050 | 2075 | 1800 | 1808 | 250 | 267 | 12.2% | 12.87%
RTU-18 | BACKROOM | 2000 | 2148 | 1700 | 1845 | 300 | 303 | 15% | 14.11%
RTU-19 | BACKROOM | 2000 | 1978 | 1700 | 1698 | 300 | 280 | 15% | 14.16%
RTU-20 | DOCK | 4000 | 4293 | 3350 | 3651 | 650 | 642 | 16.25% | 14.95%
RTU-21 | BACK OFFICES | 3000 | 3076 | 2650 | 2754 | 350 | 322 | 11.67% | 10.47%
RTU-22 | PICKUP | 3000 | 2929 | 2700 | 2617 | 300 | 312 | 10% | 10.65%
EF-G1 | OVEN | [10 empty] | 900 | 976
EF-G2 | OVEN | [10 empty] | 900 | 827
EF-K1 | HOOD | [10 empty] | 2400 | 2470
EF-CC | CLEANING | [12 empty] | 600 | 499
EF-E1 | ELEC.RM. | [12 empty] | 800 | 798
EF-E2 | ELEC. CLOSET | [12 empty] | 600 | 0
EF-R1 | ASSOC. RR | [12 empty] | 300 | 288
EF-R2 | CUST. RR | [12 empty] | 500 | 493
EF-R3 | RX/TLC | [12 empty] | 200 | 0
EF-S | SEAFOOD | [12 empty] | 800 | 781
TOTALS |  | 87940 | 82322 | 78375 | 75406 | 9565 | 6916 |  |  | 0 | 0 | 4200 | 4273 | 3800 | 2859
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL | [7 empty] | FINAL CHECKS
TOTAL OA |  | 9565 | 6916 |  | FRONT | [5 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0 | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 8000 | 7132 |  | SIDE
NET AIRFLOW |  | 1565 | -216 |  | REAR | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | TRUE
[5 empty] | AVERAGE |  | #DIV/0!
[11 empty] | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0! | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE
HD | [10 empty] | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
0