## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3500 | 3648 | 2500 | 2536 | 1000 | 1112 | 28.57% | 30.48%
RTU-2 | KITCHEN | 4800 | 4511 | 2500 | 2127 | 2300 | 2384 | 47.92% | 52.85%
FCU-1 | MANAGERS OFFICE | 450 | 432 | 400 | 385 | 50 | 47 | 11.11% | 10.88%
KEF-1 | HD1 GRILL | [10 empty] | 700 | 1115
KEF-2 | HD2 GRILL | [10 empty] | 700 | 1132
KEF-3 | HD3 FRYER | [10 empty] | 700 | 1088
KEF-4 | HD4 FRYER | [10 empty] | 700 | 1132
EF-1 | RESTROOMS | [12 empty] | 375 | 370
TOTALS |  | 8750 | 8591 | 5400 | 5048 | 3350 | 3543 |  |  | 0 | 0 | 2800 | 4467 | 375 | 370
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3350 | 3543 |  | FRONT |  | -0.0253 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3175 | 4837 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 175 | -1294 |  | REAR |  | -0.023 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.02415 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2350 | 2431
TOTAL KITCHEN EXHAUST |  | 2800 | 4467
NET AIRFLOW |  | -450 | -2036
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0