## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3500 | 3466 | 3000 | 2930 | 500 | 536 | 14.29% | 15.46%
RTU-2 | DINING | 3500 | 3561 | 2500 | 2529 | 1000 | 1032 | 28.57% | 28.98%
MUA-1 | HOOD MUA | [8 empty] | 1300 | 1302
EF-1 | HOOD FAN | [10 empty] | 2550 | 1720
EF-2 | RESTROOM | [12 empty] | 150 | 149
TOTALS |  | 7000 | 7027 | 5500 | 5459 | 1500 | 1568 |  |  | 1300 | 1302 | 2550 | 1720 | 150 | 149
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2870 |  | FRONT |  | 0.0342 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2700 | 1869 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 1001 |  | REAR |  | 0.0305 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.03235 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
Building Pressure falls above tolerance of +0.02" due to lack of exhaust flow on Hood-1. Calculations suggest once hood is remedied the building pressure should fall slightly positive and within tolerance.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0