## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | 1ST FLR DINING | 3680 | 3738 | 2630 | 2766 | 1050 | 972 | 28.53% | 26%
RTU-2 | 2ND FLR DINING | 4000 | 3834 | 3350 | 3237 | 650 | 597 | 16.25% | 15.57%
MUA-1 | COOKLINE | [8 empty] | 2250 | 2139
KEF-1 | HOODS 1&2 | [10 empty] | 3403 | 2026
EF-1 | WOMENS RR | [12 empty] | 165 | 93
EF-2 | MENS RR | [12 empty] | 165 | 97
TOTALS |  | 7680 | 7572 | 5980 | 6003 | 1700 | 1569 |  |  | 2250 | 2139 | 3403 | 2026 | 330 | 190
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3950 | 3708 |  | FRONT |  | 0.017 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3733 | 2216 |  | SIDE |  | 0.0189 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 217 | 1492 |  | REAR |  | 0.0102 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.015367 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 0
TOTAL KITCHEN EXHAUST |  | 0
NET AIRFLOW |  | 0 | 0
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0