## SUMMARY (2)
AIR BALANCE SCHEDULE
| TONS | AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT |  | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | 12.5 | SALES | 5000 | 4688 | 4000 | 3742 | 1000 | 946 | 20% | 20.18%
RTU-2 | 10 | SALES | 4000 | 3726 | 3200 | 2899 | 800 | 827 | 20% | 22.2%
RTU-3 | 10 | SALES | 4000 | 4359 | 3200 | 3527 | 800 | 832 | 20% | 19.09%
RTU-4 | 12.5 | SALES | 5000 | 4582 | 1000 | 3456 | 1000 | 1036 | 20% | 22.61%
RTU-5 | 3 | 2ND FL OFFICE NORTH | 1200 | 1231 | 1000 | 1037 | 200 | 194 | 16.67% | 15.76%
RTU-6 | UNKNOWN | 2ND FL OFFICE SOUTH | 1500 | 1504 | 1200 | 1504 | 300 | 0 | 20% | 0%
RTU-7 | 2 | SOUTH VESTIBULE | 700 | 682 | 700 | 700 | 0 | 0 | 0% | 0%
AHU-1 | UNKNOWN | BAKERY/MAIN SALES | 7020-11620 | 7061 | 5620 | 5599 | 1400 | 1462 | #VALUE! | 20.71%
AHU-2 | 1.5 | RECEIVING | 600 | 631 | 600 | 631 | 0 | 0 | 0% | 0%
EF-5 |  | KH-1 | [10 empty] | 2440 | 4868
EF-6 |  | KH-2 | [10 empty] | 2440 | 4637
MAU-3 |  | KH-1 | [8 empty] | 1000 | 1830
MAU-4 |  | KH-2 | [8 empty] | 1000 | 1703
EF-1 |  | REAR RR | [12 empty] | 324 | 324
EF-2 |  | DELI DISHWASH | [12 empty] | 250 | 250
EF-8 |  | BAKERY OVEN | [12 empty] | 1060 | 1060
EF-11 |  | FRONT RR WOMEN | [12 empty] | 36 | 36
EF-12 |  | FRONT RR MEN | [12 empty] | 62 | 62
EF-13 |  | 2ND FL RR MEN | [12 empty] | 52 | 52
EF-14 |  | 2ND FL RR WOMEN | [12 empty] | 75 | 0
TOTALS |  |  | 22000 | 28464 | 20520 | 23095 | 5500 | 5297 |  |  | 2000 | 3533 | 4880 | 9505 | 1859 | 1784
NET BUILDING AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  |  | 7500 | 8830 |  | FRONT |  | -0.0237 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  |  | 6739 | 11289 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  |  | 761 | -2459 |  | REAR |  | -0.0251 | [8 empty] | FALSE
[6 empty] | AVERAGE |  | -0.0244 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT |  | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0