## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
(E)RTU-1 | KITCHEN |  | 3054 | 0 | 2395 |  | 659 | #DIV/0! | 21.58%
(E)RTU-2 | DINING |  | 3828 | 0 | 2928 |  | 900 | #DIV/0! | 23.51%
MUA-1 | HD-1 | [9 empty] | 374
EF-1 | HD-1 | [11 empty] | 1016
EF-2 | HD-2 | [11 empty] | 0
EF-3 | RR | [13 empty] | 306
EF-4 | DINING GENERAL EXH
TOTALS |  | 0 | 6882 | 0 | 5323 | 0 | 1559 |  |  | 0 | 374 | 0 | 1016 | 0 | 306
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 0 | 1933 |  | FRONT |  | 0.003 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 0 | 1322 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 611 |  | REAR |  | 0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.003 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD-1 | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 168X12 |  | 1775 |  | 2925 |  | -1150