## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 865 | 876 | 415 | 375
RTU-2 | SALES | 865 | 869 | 415 | 417
RTU-3 | KITCHEN/SALES | 865 | 876 | 415 | 443
RTU-4 | DOCK/ELECTRICAL | 160 | 163 | 160 | 163
EF-1 | MEN'S RR |  |  |  |  | 650 | 452 | 650 | 452
EF-2 | WOMEN'S RR |  |  |  |  | 350 | 172 | 350 | 172
EF-3 | HOOD |  |  |  |  | 1350 | 1373 | 0 | 0
TOTALS |  | 2755 | 2784 | 1405 | 1398 | 2350 | 1997 | 1000 | 624
HOODS ON
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 2755 | 2784 |  |  | FRONT |  | 0.0065 |  | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2350 | 1997 |  |  | SIDE |  | 0.0001
NET AIRFLOW |  | 405 | 787 |  |  | REAR |  | 0.0005 |  | TRUE
[6 empty] | AVERAGE |  | 0.0023667
HOODS OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1405 | 1398 |  |  | FRONT |  | 0.0175
TOTAL EXHAUST |  | 1000 | 624 |  |  | SIDE |  | 0.008
NET AIRFLOW |  | 405 | 774 |  |  | REAR |  | 0.011
[6 empty] | AVERAGE |  | 0.012167
NOTES:
The left entrance doors are not sealed.