## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 2000 | 1689 |  | 1347 |  | 342 | 0% | 20.25%
RTU-2 | DINING | 5000 | 3591 |  | 2519 |  | 1072 | 0% | 29.85%
MUA | HOODS | [8 empty] | 0 | 785
EF-1 | HD1FRYER | [11 empty] | 1215
EF-2 | HD2 FRYER | [11 empty] | 1447
EF-3 | RESTROOM | [13 empty] | 0
EF-4 | RESTROOM | [13 empty] | 0
TOTALS |  | 7000 | 5280 | 0 | 3866 | 0 | 1414 |  |  | 0 | 785 | 0 | 2662 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 0 | 2199 |  | FRONT |  | -0.005 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 0 | 2662 |  | SIDE |  |  | -0.0048 |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | -463 |  | REAR |  | -0.0042 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0046 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0