## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING ROOM | 3000 | 3012 | 2325 | 2278 | 675 | 734 | 22.5% | 24.37%
RTU-2 | DINING ROOM | 3000 | 3149 | 2325 | 2452 | 675 | 697 | 22.5% | 22.13%
RTU-3 | DINING/OFFICE | 4000 | 4031 | 3100 | 3112 | 900 | 919 | 22.5% | 22.8%
RTU-4 | DINING ROOM | 3000 | 3110 | 2325 | 2395 | 675 | 715 | 22.5% | 22.99%
RTU-5 | KITCHEN | 3000 | 3107 | 2325 | 2396 | 675 | 711 | 22.5% | 22.88%
PRV 2 | HOOD-1 | [10 empty] | 1500 | 1542
PRV4 | HOOD-2 | [10 empty] | 1500 | 1476
PRV 4 | HOOD-3 | [10 empty] | 500 | 526
PRV1 | RESTROOMS | [12 empty] | 525 | 515
EFA1 | MOP SINK | [12 empty] | 75 | 79
RTU-6 | EXISTING BOH |  |  |  |  | 500 | 512
TOTALS |  | 16000 | 16409 | 12400 | 12633 | 4100 | 4288 |  |  | 0 | 0 | 3500 | 3544 | 600 | 594
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4100 | 4288 |  | FRONT |  | 0.0064 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4100 | 4138 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 150 |  | REAR |  | 0.0023 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00435 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0