## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3000 | 3116 | 2500 | 2567 | 500 | 549 | 16.67% | 17.62%
RTU-2 | DINING | 3000 | 2898 | 2000 | 1901 | 1000 | 997 | 33.33% | 34.4%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 2109
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3272
EF-2 | RESTROOM | [12 empty] | 200 | 197
TOTALS |  | 6000 | 6014 | 4500 | 4468 | 1500 | 1546 |  |  | 1950 | 2109 | 3200 | 3272 | 200 | 197
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3655 |  | FRONT |  | 0.0012 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3400 | 3469 |  | SIDE |  | 0.003 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 186 |  | REAR |  | 0.0297 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0113 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Pressure on the read door is elevated due to diffuser 1-3 affecting the measurement. That diffuser is high on flow and blowing on the back door. There did not appear to be any issue with the operation of the back door.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250