## Report Sheet
STORE #: | 4078 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | SHAKER HEIGHTS, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-05 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
CARRIER | 48TCEM90A2A5 | 2322P44823 | RTU-1 | KITCHEN | 500 | 421 | 0 | 0 |  | 1681 | 1681 | 939 | 939 | NL | 205.5 | 205.5 | 3 | 6.9 | 6.54 | 6.54 | 2.2466 | 2.2466 | 0%
ARRIER | 48FCEM12A3A5 | 2922P79703 | RTU-2 | DINING | 1000 | 994 | 1000 | 994 |  | 1866 | 1866 | 1866 | 1866 | NL | 204.5 | 204.5 | 3 | 12.6 | 5.31 | 5.31 | 1.8152 | 1.8152 | 0%
CAPTIVE AIRE | A1-D.250-15D | 5581314 | MUA-1 | HOOD 1 | 1950 | 1724 | 1700 | 1724 | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0%
CAPTIVE AIRE | DU240HFA | 5581314 | EF-1 | HOOD 1 | 3200 | 2980 | 2450 | 2559 | No | 1191 | 1046 | 1191 | 1046 | 3 | 207.9 | 208 | 3 | 9.2 | 6.1 | 5.3 | 2.12 | 1.8428 | -13.07%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 3139 | 2700 | 2718 |  | FRONT DOOR |  | -0.0012 |  |  | INITIAL | 6.1818 | 3139
|  |  | TOTAL EXHAUST |  | 3350 | 3130 | 2600 | 2709 |  | BACK DOOR |  | -0.0075 |  |  | FINAL | 5.9047 | 5277
|  |  | NET AIRFLOW |  | 100 | 9 | 100 | 9 |  | AVERAGE |  | -0.00435 |  |  | ∆ | 0.27714 | -2138
Issue List
Unit # | Description
Select from drop down list
RTU-2 | RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
MUA | Suspect MUA filters are dirty, CFM fell withign design but set point of 70.6 makes me think it's operating at a higher amperage than would reflect the measured CFM of 1724
MUA | MUA inaccesible, unable to read Volts, Amps, or record unit data

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.