## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FCU-1 | SUNROOM DINING | 6000 | 6042 | 6000 | 6042 | 0 | 0 | 0% | 0%
FCU-2 | ENTRY DINING | 6000 | 5936 | 6000 | 5936 | 0 | 0 | 0% | 0%
FCU-3 | BOH | 6000 | 5995 | 6000 | 5995 | 0 | 0 | 0% | 0%
FCU-4 | PRIVATE DINING | 1200 | 1318 | 1200 | 1318 | 0 | 0 | 0% | 0%
SF-1 | OA | 1850 | 1391 | 0 | 0 | 1850 | 1391 | 100%
OSA-1 | OA | 2500 | 2610 | 0 | 0 | 2500 | 2610 | 100% | 100%
MUA-1 | MUA | [8 empty] | 6200 | 6124
KEF-1 | 1A & 1B | [10 empty] | 4350 | 4091
KEF-2 | HOOD 2 | [10 empty] | 3400 | 3667
KEF-3 | DW | [10 empty] | 1400 | 981
EF-4 | RR | [12 empty] | 450 | 371
6217 |  | 23550 | 23292 | 19200 | 19291 | 4350 | 4001 |  |  | 6200 | 6124 | 9150 | 8739 | 450 | 371
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 10550 | 10125 |  | FRONT |  | 0.015 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 9600 | 9110 |  | SIDE |  | 0.01 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 950 | 1015 |  | REAR |  | 0.02 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.015 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0