## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | STORAGE | 1750 | 1686 | 1600 | 1531 | 150 | 155 | 8.571% | 9.193%
RTU-2 | WEST SALES | 2800 | 2869 | 2150 | 2243 | 650 | 626 | 23.21% | 21.82%
RTU-3 | EAST SALES | 2800 | 2889 | 2150 | 2225 | 650 | 664 | 23.21% | 22.98%
RTU-4 | SOUTH SALES | 3500 | 3584 | 2725 | 2826 | 775 | 758 | 22.14% | 21.15%
EF-1 | RESTROOM | [12 empty] | 75 | 70
EF-2 | RESTROOM | [12 empty] | 75 | 78
TOTALS |  | 10850 | 11028 | 8625 | 8825 | 2225 | 2203 |  |  | 0 | 0 | 0 | 0 | 150 | 148
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2225 | 2203 |  | FRONT |  | 0.0243" | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 150 | 148 |  | SIDE |  | 0.0238" |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 2075 | 2055 |  | REAR |  | 0.0234" | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0238 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.03" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0