NTI Internal ONLY

King Soopers 620-154

Cody Collett 04/14/2025

Day one

Arrived on site

Completed initial walkthrough of site on the roof

Examined current data from previous tech

Corrected incorrect/incomplete data from previous tech

Created punch list of 20 or so items

Rough punch list:

most exhaust fans don’t have power.

Hinge kits incorrect or obstructed by flex and/or grease trap.

Multiple backdraft dampers don’t open due to being installed too close to fan

Multiple EF’s have either homemade curb adapter which are poorly fit and have large gaps causing leakage or curb adapters are not installed snugly to the curb creating leakage.

Deli hoods missing filter (acquired later)  Missing end panels. Foam wrapping is still on exhaust DUCT temp sensor

Both DOAS turned off at disconnect and visibly missing parts.

Sent out punch list on scheduling email.

Day two

Contacted site super to discuss issue list

Walked through issue list with Site super’s subordinates

Walked spaces and examined ductwork from ground level to ensure all diffusers were installed and viewed into diffusers from ground level to see if flex duct was actually attached.

RTU-12 missing diffuser 1

RTU-8 missing diffuser 3

RTU-10 missing diffuser 12

Balanced as many drop down units as possible.

RTU-18 no power and no disconnect switch

Continued balancing

Found and documented obstructive flex duct on unit that were in the process of being balanced.

Day 3

Continued balancing

Set total CFM for RTU-8 via return due to damper installed in main supply drop prevented a good traverse location.

Day 4 (Final day on site)

Continued balancing

Remaining Items

Doas 1

Doas 2

RTU-3 (No power)

RTU-12 (Missing Diffuser)

RTU-18 (No power, Missing Disconnect)

RTU-16 (Airflow leakage above ceiling and on the roof)

All EF’s (10 Total)