## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 4565 | 4526 | 4565 | 4526 | 0 | 0 | 0% | 0%
RTU-2 | SALES | 4395 | 4325 | 4395 | 4325 | 0 | 0 | 0% | 0%
RTU-3 | SALES | 3925 | 4054 | 3925 | 4054 | 0 | 0 | 0% | 0%
RTU-4 | SALES | 4350 | 4290 | 4350 | 4290 | 0 | 0 | 0% | 0%
RTU-5 | SALES | 4635 | 4862 | 4635 | 4862 | 0 | 0 | 0% | 0%
RTU-6 | SALES | 4075 | 4316 | 4075 | 4316 | 0 | 0 | 0% | 0%
RTU-7 | SALES | 4290 | 4327 | 4290 | 4327 | 0 | 0 | 0% | 0%
RTU-8 | SALES | 4100 | 3850 | 3526 | 3850 | 574 | 0 | 14% | 0%
RTU-9 | SALES | 3720 | 3634 | 3720 | 3634 | 0 | 0 | 0% | 0%
RTU-10 | PHARMACY | 2070 | 2209 | 1560 | 1667 | 510 | 542 | 24.64% | 24.54%
RTU-11 | DELI | 1990 | 1892 | 1818 | 1712 | 172 | 180 | 8.643% | 9.514%
RTU-12 | BAKERY | 1600 | 1594 | 1600 | 1594 | 0 | 0 | 0% | 0%
RTU-13 | BACKROOM | 2060 | 1965 | 1865 | 1787 | 195 | 178 | 9.466% | 9.059%
RTU-14 | BACKROOM | 1900 | 2041 | 1627 | 1754 | 273 | 287 | 14.37% | 14.06%
RTU-15 | DOCK | 3225 | 3200 | 2635 | 2668 | 590 | 532 | 18.29% | 16.62%
RTU-16 | OFFICES | 2915 | 2883 | 2308 | 2297 | 607 | 586 | 20.82% | 20.33%
RTU-17 | PICKUP | 2800 | 2840 | 2387 | 2455 | 413 | 385 | 14.75% | 13.56%
RTU-18 | VESTIBULE | 3500 | 3241 | 3500 | 3241 | 0 | 0 | 0% | 0%
RTU-19 | VESTIBULE | 3500 | 3726 | 3500 | 3726 | 0 | 0 | 0% | 0%
DOAS-1 | SALES FLOOR | [8 empty] | 6050 | 5805
DOAS-2 | SALES FLOOR | [8 empty] | 6050 | 6191
EF-1 | CUSTOMER RR | [12 empty] | 700 | 810
EF-2 | TLC | [12 empty] | 200 | 198
EF-3 | EMPLOYEE RR | [12 empty] | 500 | 510
EF-4 | DELI HOOD | [10 empty] | 2400 | 2534
EF-5 | ELECTRICAL | [12 empty] | 800 | 824
EF-6 | ELECTRICAL | [12 empty] | 800 | 815
EF-7 | SEAFOOD | [12 empty] | 700 | 715
EF-8 | CLEANING CENTER | [12 empty] | 200 | 207
EF-9 | BAKERY OVEN | [12 empty] | 600 | 595
EF-10 | BAKERY OVEN | [12 empty] | 600 | 553
TOTALS |  | 63615 | 63775 | 60281 | 61085 | 3334 | 2690 |  |  | 12100 | 11996 | 2400 | 2534 | 5100 | 5227
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 15434 | 14686 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 7500 | 7761 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 7934 | 6925 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0