## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 4565 |  | 4565 | 0 | 0 |  | 0% | #DIV/0!
RTU-2 | SALES | 4395 |  | 4395 | 0 | 0 |  | 0% | #DIV/0!
RTU-3 | SALES | 3925 |  | 3925 | 0 | 0 |  | 0% | #DIV/0!
RTU-4 | SALES | 4350 |  | 4350 | 0 | 0 |  | 0% | #DIV/0!
RTU-5 | SALES | 4635 |  | 4635 | 0 | 0 |  | 0% | #DIV/0!
RTU-6 | SALES | 4075 |  | 4075 | 0 | 0 |  | 0% | #DIV/0!
RTU-7 | SALES | 4290 |  | 4290 | 0 | 0 |  | 0% | #DIV/0!
RTU-8 | SALES | 4100 |  | 3526 | 0 | 574 |  | 14% | #DIV/0!
RTU-9 | SALES | 3720 |  | 3720 | 0 | 0 |  | 0% | #DIV/0!
RTU-10 | PHARMACY | 2070 |  | 1560 | 0 | 510 |  | 24.64% | #DIV/0!
RTU-11 | DELI | 1990 |  | 1818 | 0 | 172 |  | 8.643% | #DIV/0!
RTU-12 | BAKERY | 1600 |  | 1600 | 0 | 0 |  | 0% | #DIV/0!
RTU-13 | BACKROOM | 2060 |  | 1865 | 0 | 195 |  | 9.466% | #DIV/0!
RTU-14 | BACKROOM | 1900 |  | 1627 | 0 | 273 |  | 14.37% | #DIV/0!
RTU-15 | DOCK | 3225 |  | 2635 | 0 | 590 |  | 18.29% | #DIV/0!
RTU-16 | OFFICES | 2915 |  | 2308 | 0 | 607 |  | 20.82% | #DIV/0!
RTU-17 | PICKUP | 2800 |  | 2387 | 0 | 413 |  | 14.75% | #DIV/0!
RTU-18 | VESTIBULE | 3500 |  | 3500 | 0 | 0 |  | 0% | #DIV/0!
RTU-19 | VESTIBULE | 3500 |  | 3500 | 0 | 0 |  | 0% | #DIV/0!
DOAS-1 | [9 empty] | 6050
DOAS-2 | [9 empty] | 6050
EF-1 | [13 empty] | 700
EF-2 | [13 empty] | 200
EF-3 | [13 empty] | 500
EF-4 | [13 empty] | 2400
EF-5 | [13 empty] | 800
EF-6 | [13 empty] | 800
EF-7 | [13 empty] | 700
EF-8 | [13 empty] | 200
EF-9 | [11 empty] | 600
EF-10 | [11 empty] | 600
TOTALS |  | 63615 | 0 | 60281 | 0 | 3334 | 0 |  |  | 12100 | 0 | 1200 | 0 | 6300 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 15434 | 0 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 7500 | 0 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 7934 | 0 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0