## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4375 | 3786 | 3875 | 3291 | 500 | 495 | 11.43% | 13.07%
RTU-2 | DINING | 3750 | 3768 | 2750 | 2746 | 1000 | 1022 | 26.67% | 27.12%
MUA-1 | KITCHEN HD | [8 empty] | 1300 | 1261
EF-1 | KITCHEN HD | [10 empty] | 2550 | 2492
EF-2 | RESTROOM | [12 empty] | 150 | 149
TOTALS |  | 8125 | 7554 | 6625 | 6037 | 1500 | 1517 |  |  | 1300 | 1261 | 2550 | 2492 | 150 | 149
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2778 |  | FRONT |  | -0.0009 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 2700 | 2641 |  | SIDE |  | -0.0026 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 100 | 137 |  | REAR |  | -0.0034 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0023 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Building pressure is -0.0033 with no equipment on. Net store pressurization -0.0010
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0