## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8500 | 8363 | 6500 | 6235 | 2000 | 2128 | 23.53% | 25.45%
AC-2 | SIDE DINING | 2830 | 2603 | 2080 | 1861 | 750 | 742 | 26.5% | 28.51%
AC-3 | DRIVE THRU | 4000 | 4068 | 3000 | 3009 | 1000 | 1059 | 25% | 26.03%
AC-4 | MAIN DINING | 2765 | 2906 | 2165 | 2338 | 600 | 568 | 21.7% | 19.55%
AC-5 | PLAY AREA | 1800 | 1935 | 1500 | 1620 | 300 | 315 | 16.67% | 16.28%
AC-6 | BOH |  |  | 0
EF-1 | HD 1 | [10 empty] | 1913 | 2010
EF-2 | HD 2 & 3 | [10 empty] | 1402 | 1529
EF-3 | RESTROOMS | [12 empty] | 400 | 391
EF4 | RESTROOMS
EF 5 | HD L1
TOTALS |  | 19895 | 19875 | 15245 | 15063 | 4650 | 4812 |  |  | 0 | 0 | 3315 | 3539 | 400 | 391
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4812 |  | FRONT |  | 0.013 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3715 | 3930 |  | SIDE |  | 0.016 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 935 | 882 |  | REAR |  | 0.014 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.014333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390