## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3351 | 2900 | 2774 | 500 | 577 | 14.71% | 17.22%
RTU-2 | DINING | 4000 | 3817 | 3000 | 2845 | 1000 | 972 | 25% | 25.47%
MUA-1 | KITCHEN HD | [8 empty] | 1300 | 1394
EF-1 | KITCHEN HD | [10 empty] | 2550 | 2566
EF-2 | RESTROOM | [12 empty] | 150 | 143
TOTALS |  | 7400 | 7168 | 5900 | 5619 | 1500 | 1549 |  |  | 1300 | 1394 | 2550 | 2566 | 150 | 143
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2943 |  | FRONT |  | -0.006 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 2700 | 2709 |  | SIDE |  | -0.0023 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 100 | 234 |  | REAR |  | -0.0022 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0035 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0