## RTU-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: RTU-3 (FLOOR 1)
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual |  | Schedule
Model Num | YSJ120A3SOM05E | SF CFM | 3580 | 3738 |  | 3155
Serial Num | 24150950L | SF RPM |  | NA
Configuration | VERTICAL | RA CFM | 2791 | 2955
Num OA Filters | 1 | OA CFM | 789 | 783
OA Filter Size | 16"X36" | RL VOLTAGE | 208 | 208
Num PreFilter 1 | 3 | RL AMPERAGE |  | 6.7/7.1/5.4 | 6.4AVG
Num PreFilter 2 | 2 | OA Damper Position |  | 15%
PreFilter Size 1 | 16"X24"X2" | Brake Horsepower | 3 | 2.181
PreFilter Size 2 | 18"X24"X2"
Motor Data |  | Performance Data
Motor MFG | NL |  | Design | Actual
Frame | NL | Fan Suction SP |  | -0.93"
Horsepower | 3 | Fan Discharge SP |  | 0.43"
Motor RPM | NL | Fan Total SP |  | 1.34
Phase | 3 | DX Coil PD * |  | * |  | MIXED AIR SP -0.38"
Rated Voltage | 208 | Pre Filter PD |  | *combined
Rated Amperage | 8.8 | Total ESP | 1 | 0.81"
Service Factor | NL
NOTE: SCHEDULE FOR RTU-3 IS 3155 CFM, DIFFUSER TOTAL IS 3580 CFM

## RTU-3 SGRD
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: RTU-3 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
3-1 | 115 | LD-1 | 8 | 220 | 189 | 189 | 0.85909 | Notes: No dampers installed on linear diffusers, unable to balance airflow.
3-2 | 115 | LD-1 | 8 | 220 | 205 | 205 | 0.93182
3-3 | 115 | LD-1 | 8 | 220 | 194 | 194 | 0.88182
3-4 | 115 | LD-1 | 8 | 220 | 195 | 195 | 0.88636
3-5 | 115 | LD-1 | 8 | 220 | 245 | 245 | 1.1136
3-6 | 115 | LD-1 | 8 | 220 | 248 | 248 | 1.1273
3-7 | 115 | LD-1 | 8 | 215 | 196 | 196 | 0.91163
3-8 | 115 | LD-1 | 8 | 215 | 239 | 239 | 1.1116
3-9 | 115 | LD-1 | 8 | 215 | 219 | 219 | 1.0186
3-10 | 115 | LD-1 | 8 | 215 | 228 | 228 | 1.0605
3-11 | 115 | LD-1 | 8 | 220 | 222 | 222 | 1.0091
3-12 | 115 | LD-1 | 8 | 220 | 226 | 226 | 1.0273
3-13 | 115 | LD-1 | 8 | 220 | 270 | 270 | 1.2273
3-14 | 115 | LD-1 | 8 | 220 | 239 | 239 | 1.0864
3-15 | 115 | LD-1 | 8 | 220 | 275 | 275 | 1.25
3-16 | 115 | LD-1 | 8 | 220 | 268 | 268 | 1.2182
3-17 | 120 | SR-4 | 4 | 10 | 9 | 9 | 0.9
3-18 | 116 | SR-4 | 4 | 20 | 21 | 21 | 1.05
3-19 | 119 | SR-4 | 4 | 10 | 11 | 11 | 1.1
3-20 | 118 | SR-4 | 6 | 40 | 39 | 39 | 0.975
RTU-3 |  |  |  | 3580 |  | 3738 | 1.0441

## RTU-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: RTU-4 (FLOOR 1)
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual |  | Schedule
Model Num | YSJ102A3S0M05E | SF CFM | 3140 | 3266 |  | 3630
Serial Num | 241212072L | SF RPM |  | NA
Configuration | VERTICAL | RA CFM | 2286 | 2404
Num OA Filters | 1 | OA CFM | 854 | 862
OA Filter Size | 16"X36" | RL VOLTAGE | 208 | 208
Num PreFilter 1 | 3 | RL AMPERAGE |  | 4.9/3.0/4.5 | 4.13AVG
Num PreFilter 2 | 2 | OA Damper Position |  | 15%
PreFilter Size 1 | 16"X24"X2" | Brake Horsepower | 3 | 1.407
PreFilter Size 2 | 18"X24"X2"
Motor Data |  | Performance Data
Motor MFG | NL |  | Design | Actual
Frame | NL | Fan Suction SP |  | -0.57"
Horsepower | NL | Fan Discharge SP |  | 0.47"
Motor RPM | NL | Fan Total SP |  | 1.04" |  | MIXED AIR SP -0.26"
Phase | 3 | DX Coil PD * |  | *
Rated Voltage | 208 | Pre Filter PD |  | *combined
Rated Amperage | 8.8 | Total ESP | 1 | 0.73"
Service Factor | NL

## RTU-4 SGRD
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: RTU-4 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
4-1 | 114 | SR-4 | 4 | 20 | 85 | 22 | 1.1
4-2 | 113 | SR-4 | 4 | 20 | 105 | 21 | 1.05
4-3 | 120 (1) | SR-4 | 4 | 10 | 142 | 10 | 1
4-4 | 119 (1) | SR-4 | 4 | 10 | 108 | 9 | 0.9
4-5 | 121 | SR-4 | 6 | 60 | 222 | 56 | 0.93333
4-6 | 112 | SR-4 | 6 | 20 | 185 | 19 | 0.95
4-7 | 111 | CD-1 | 10 | 375 | 322 | 394 | 1.0507
4-8 | 111 | CD-1 | 10 | 375 | 306 | 406 | 1.0827
4-9 | 111 | CD-1 | 10 | 375 | 315 | 381 | 1.016
4-10 | 111 | CD-1 | 10 | 375 | 289 | 396 | 1.056
4-11 | 111 | CD-1 | 10 | 375 | 299 | 389 | 1.0373
4-12 | 111 | CD-1 | 10 | 375 | 315 | 355 | 0.94667
4-13 | 111 | CD-1 | 10 | 375 | 326 | 399 | 1.064
4-14 | 111 | CD-1 | 10 | 375 | 305 | 409 | 1.0907
RTU-4 |  |  |  | 3140 | 3324 | 3266 | 1.0401

## EF-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: EF-1 |  |  | Area: FLOOR 1
Unit Data |  |  |  |  | Drive Data
MFG |  | COOK |  |  | Motor Sheave Size | 3 1/4"
Model Num |  | 100CPVCL1100CPV |  |  | Motor Bore Size | 1/2" |  | MOTOR RPM 1781
Serial Num |  | 108SL14374-00/0000701 |  |  | Fan Sheave Size | 3 1/2" |  | FAN RPM 1126
Type |  | UTILITY SET FAN |  |  | Fan Bore Size | 3/4"
[5 empty] | Belt CL Distance | 15"
Motor Data |  |  |  |  | No of Belts | 1
Motor MFG |  | US MOTORS |  |  | Belt Size | A31
Frame |  | NL
Horsepower |  | 0.33 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 270 | 272
Amperage (rated) |  | 6 |  |  | RL Voltage | 120 | 122
Service Factor |  | 1.35 |  |  | RL Amperage |  | 5.3
[5 empty] | Suction ESP |  | -0.12"
[5 empty] | Total ESP | 0.4 | 0.12"
[5 empty] | Brake Horse Power | 0.04
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E1-1 | 120 | ER-1 | 8 | 70 | 93 | 65 | 0.92857
E1-2 | 119 | ER-1 | 8 | 70 | 83 | 69 | 0.98571
E1-3 | 113 | ER-1 | 4 | 35 | 554 | 34 | 0.97143
E1-4 | 114 | ER-1 | 6 | 70 | 20 | 72 | 1.0286
E1-5 | 122 | ER-1 | 4 | 10 | 20 | 11 | 1.1
E1-6 | 119 | ER-1 | 4 | 10 | 23 | 10 | 1
E1-7 | 121 | ER-1 | 6 | 10 | 60 | 11 | 1.1
|  |  |  | 275 | 853 | 272 | 0.98909
-

## FCU03-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU03-1 (FCU-G1) |  | Area: 305
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Unit only rated for 2200 CFM per submitals.
Model Num | HPPR022 |  |  |  | SA CFM | 2580 | 2135
Serial Num | 356318-1 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2580 | 2179
Motor Data |  |  |  |  | RL Voltage |  | 121.2
Motor MFG | NL |  |  |  | RL Amperage |  | 6.8
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.53"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.16"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.69"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F31-1 | BED 1 | SR | 10 | 380 | 303 | 303 | 0.79737
F31-2 | BED 2 | SR | 10 | 300 | 266 | 266 | 0.88667
F31-3 | BED 2 | SR | 10 | 300 | 254 | 254 | 0.84667
F31-4 | LIVING | SR | 10 | 320 | 218 | 218 | 0.68125
F31-5 | LIVING | SR | 10 | 320 | 324 | 324 | 1.0125
F31-6 | LIVING | SR | 10 | 320 | 286 | 286 | 0.89375
F31-7 | LIVING | SR | 10 | 320 | 264 | 264 | 0.825
F31-8 | LIVING | SR | 10 | 320 | 220 | 220 | 0.6875
SA TOTAL |  |  |  | 2580 |  | 2135 | 0.82752
R31-1 |  | RR | 28X28 | 2580 | 2179 | 2179
RA TOTAL |  |  |  | 2580 |  | 2179 | 0.84457
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU03-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU03-2 (FCU-Q) |  | Area: 301
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR010 |  |  |  | SA CFM | 990 | 983
Serial Num | 356318-5 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 990 | 933
Motor Data |  |  |  |  | RL Voltage |  | NA
Motor MFG | NL |  |  |  | RL Amperage |  | NA
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.56"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.20"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.76
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Fan speed set to highest set pt.
F32-1 | STUDIO | SR | 10 | 330 | 304 | 339 | 1.0273
F32-2 | STUDIO | SR | 10 | 330 | 248 | 310 | 0.93939
F32-3 | STUDIO | SR | 10 | 330 | 267 | 334 | 1.0121
SA TOTAL |  |  |  | 990 |  | 983 | 0.99293
R32-1 |  | RR | 18X18 | 990 | 707 | 933 | 0.94242
RA TOTAL |  |  |  | 990 |  | 933 | 0.94242
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU03-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU03-3 (FCU-B1) |  | Area: 302
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR015W4R411L000 |  |  |  | SA CFM | 1740 | 1371
Serial Num | 356318-3 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1371
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 7 | NOTE: Amperage is for both motors.
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.07" | Unit only rated for 1500 CFM based on submitals
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.12"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.19"
Voltage (rated) | 120 |  |  |  | Brake HP |  |  |  | Fan suction after filters -0.42"
Amperage (rated) | 5 | [7 empty] | fan discharge before coil 0.55"
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F33-1 | LIVING | SR | 10 | 305 | 199 | 196 | 0.64262
F33-2 | LIVING | SR | 10 | 310 | 246 | 231 | 0.74516
F33-3 | LIVING | SR | 10 | 305 | 241 | 250 | 0.81967
F33-4 | BED | SR | 10 | 275 | 200 | 245 | 0.89091
F33-5 | BED | SR | 10 | 270 | 267 | 238 | 0.88148
F33-6 | BED | SR | 10 | 275 | 221 | 211 | 0.76727
SA TOTAL |  |  |  | 1740 | 1374 | 1371 | 0.78793
R33-1 |  | RR | 22X22 | 1740 | 1374 | 1371 | 0.78793
RA TOTAL |  |  |  | 1740 | 1374 | 1371 | 0.78793
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU03-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU03-4 (FCU-D) |  | Area: 307
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R321R000 |  |  |  | SA CFM | 670 | 713
Serial Num | 356318-6 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 670 | 713
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 4.6
Horsepower | 0.33 |  |  |  | Suction ESP |  | 0.82"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.22" | RETURN DUCT SUCTION -0.11"
Phase | 1 |  |  |  | Total ESP | 0.4 | 1.04" | BEFORE COIL DISCHARGE 0.60"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.303
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F34-1 | LIVING | SR | 10 | 305 | 347 | 289 | 0.94754 | Notes: Unable to increase diffuser 2, diffuser 2 does not increase when diffusers 1 and 3 are fully closed; most likely cause is a restrictive or obstructed duct on diffuser 2. Closed damper 3 as much as possible without it whistleing loudly.
F34-2 | LIVING | SR | 10 | 305 | 125 | 134 | 0.43934
F34-3 | LIVING | SR | 10 | 60 | 253 | 290 | 4.8333
SA TOTAL |  |  |  | 670 | 725 | 713 | 1.0642
R34-1 |  | RR | 16X16 | 670 | 725 | 713 | 1.0642
RA TOTAL |  |  |  | 670 | 725 | 713 | 1.0642
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU03-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU03-5 (FCU-E) |  | Area: 308
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211R000 |  |  |  | SA CFM | 370 | 458
Serial Num | 356318-7 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 370 | 458
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 1.43
Horsepower | 0.33 |  |  |  | Suction ESP |  | 0.08"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.17"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.25"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.094
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F35-1 | LIVING | SR | 10 | 310 | 234 | 341 | 1.1 | Notes: Prelim CFM at low speed, final CFM at medium speed. Cannot reduce F35-2 any further, damper fully closed.
F35-2 | LIVING | SR | 10 | 60 | 62 | 117 | 1.95
SA TOTAL |  |  |  | 370 | 296 | 458 | 1.2378
R35-1 |  | RR | 12X12 | 370 | 296 | 458 | 1.2378
RA TOTAL |  |  |  | 370 | 296 | 458 | 1.2378
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU03-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU03-6 (FCU-B2) |  | Area: 303
Unit Data |  |  |  |  | Test Data |  |  | Issues
MFG | WHALEN |  |  |  |  | Design | Actual | Unit filters clogged, removal of filter increased airflow from 719 to 1317. Obstruction caused by excesive sawdust, space was used as a woodworking shop. Unit only rated for 1500 CFM
Model Num | HPPR015W4R411R000 |  |  |  | SA CFM | 1740 | 1317
Serial Num | 356318-4 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1317
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 5
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.19"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.11
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.3
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.165
Amperage (rated) | 5
MOTOR QTY |  | 2 |  |  | Note: Pressures and airflow obtained without filters installed
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F36-1 | BED | SR | 10 | 275 | 124 | 227 | 0.82545
F36-2 | BED | SR | 10 | 270 | 90 | 216 | 0.8
F36-3 | BED | SR | 10 | 275 | 80 | 208 | 0.75636
F36-4 | LIVING | SR | 10 | 305 | 136 | 221 | 0.72459
F36-5 | LIVING | SR | 10 | 305 | 177 | 230 | 0.7541
F36-6 | LIVING | SR | 10 | 310 | 112 | 215 | 0.69355
SA TOTAL |  |  |  | 1740 | 719 | 1317 | 0.7569
R36-1 |  | RR | 24X24 | 1740 | 719 | 1317 | 0.7569
RA TOTAL |  |  |  | 1740 | 719 | 1317 | 0.7569
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU03-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU03-7 (FCU-F) |  | Area: 310
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R421R00 |  |  |  | SA CFM | 780 | 744
Serial Num | 356315-8 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 780
Motor Data |  |  |  |  | RL Voltage |  | 124.3
Motor MFG | NA |  |  |  | RL Amperage |  | 4.8
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.48"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.13"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.61"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Fan speed is set to highest pt.
F37-1 | BED | SR | 10 | 230 | 216 | 216 | 0.93913 | Return grille not installed, unable to read return flow.
F37-2 | LIVING | SR | 10 | 180 | 187 | 187 | 1.0389
F37-3 | LIVING | SR | 10 | 185 | 171 | 171 | 0.92432
F37-4 | LIVING | SR | 10 | 185 | 170 | 170 | 0.91892
SA TOTAL |  |  |  | 780 | 744 | 744 | 0.95385
R37-1 |  | RR | 16X16 | 780 |  |  | 0
RA TOTAL |  |  |  | 780 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU03-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU03-8 (FCU-LOBBY) |  | Area: 319
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006 |  |  |  | SA CFM | 370 | 400
Serial Num | 356318-9 |  |  |  | Fan RPM |  | MED
[5 empty] | OA CFM | 0 | NA
[5 empty] | RA CFM | 200 | 400
Motor Data |  |  |  |  | RL Voltage |  | 120
Motor MFG | NA |  |  |  | RL Amperage |  | 2
Horsepower | 0.333 |  |  |  | Suction ESP |  | -0.71
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.12
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.83
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.13
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F38-1 | 519 | CD-1 |  | 200 | 170 | 214 | 1.07
F38-2 | 518 | SR-Z |  | 110 | 173 | 121 | 1.1
F38-3 | 517 | SR-ZA |  | 60 | 25 | 65 | 1.0833
SA TOTAL |  |  |  | 370 | 368 | 400 | 1.0811
R38-1 | 519 | RR-9 | 8 | 200 |  |  | 0
RA TOTAL |  |  |  | 200 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU03-9
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU03-9 (FCU-A2) |  | Area: 304
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Missing supply and return grills. 12/30/2024
Model Num |  |  |  |  | SA CFM | 2430
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 0
[5 empty] | RA CFM | 2430
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP | 0.4
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F39-1 | BED | SR | 10 | 255 |  |  | 0
F39-2 | BED | SR | 10 | 255 |  |  | 0
F39-3 | LIVING | SR | 10 | 320 |  |  | 0
F39-4 | LIVING | SR | 10 | 320 |  |  | 0
F39-5 | LIVING | SR | 10 | 320 |  |  | 0
F39-6 | LIVING | SR | 10 | 320 |  |  | 0
F39-7 | LIVING | SR | 10 | 320 |  |  | 0
F39-8 | LIVING | SR | 10 | 320 |  |  | 0
SA TOTAL |  |  |  | 2430 |  | 0 | 0
R39-1 |  | RR | 30X30 | 2430 |  |  | 0
RA TOTAL |  |  |  | 2430 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU04-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU04-1 (FCU-G1) |  | Area: 405
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022 |  |  |  | SA CFM | 2580 | 2000
Serial Num | 356318-1 |  |  |  | Fan RPM |  | NA | High speed setpoint
[5 empty] | OA CFM | 0 | 0 | fan undersized can only do 2200 CFM based on submitals
[5 empty] | RA CFM | 2580 | 2000
Motor Data |  |  |  |  | RL Voltage |  | 121.5
Motor MFG | NL |  |  |  | RL Amperage |  | 6.9
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.53"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.18"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.71"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Unit below design with fan speed set to highest set pt.
F41-1 | BED 1 | SR | 10 | 380 | 278 | 278 | 0.73158
F41-2 | BED 2 | SR | 10 | 300 | 222 | 222 | 0.74
F41-3 | BED 2 | SR | 10 | 300 | 236 | 236 | 0.78667
F41-4 | LIVING | SR | 10 | 320 | 252 | 252 | 0.7875
F41-5 | LIVING | SR | 10 | 320 | 251 | 251 | 0.78438
F41-6 | LIVING | SR | 10 | 320 | 252 | 252 | 0.7875
F41-7 | LIVING | SR | 10 | 320 | 263 | 263 | 0.82188
F41-8 | LIVING | SR | 10 | 320 | 246 | 246 | 0.76875
SA TOTAL |  |  |  | 2580 | 2000 | 2000 | 0.77519
R41-1 |  | RR | 28X28 | 2580 | 2000 | 2000
RA TOTAL |  |  |  | 2580 |  | 2000 | 0.77519
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU04-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU04-2 (FCU-Q) |  | Area: 401
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR0010 |  |  |  | SA CFM | 990 | 928
Serial Num | 356318-5 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 990 | 972
Motor Data |  |  |  |  | RL Voltage |  | 127.9
Motor MFG | NL |  |  |  | RL Amperage |  | 7.07
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.48"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.21"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.69"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.459
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Fan speed at highest set pt.
F42-1 | STUDIO | SR | 10 | 330 | 309 | 309 | 0.93636
F42-2 | STUDIO | SR | 10 | 330 | 298 | 298 | 0.90303
F42-3 | STUDIO | SR | 10 | 330 | 321 | 321 | 0.97273
SA TOTAL |  |  |  | 990 |  | 928 | 0.93737
R42-1 |  | RR | 18X18 | 990 | 972 | 972 | 0.98182
RA TOTAL |  |  |  | 990 |  | 972 | 0.98182
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU04-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU04-3 (FCU-B1) |  | Area: 402
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPRO15 |  |  |  | SA CFM | 1740 | 1412
Serial Num | 356318-3 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1487
Motor Data |  |  |  |  | RL Voltage |  | 122.7
Motor MFG | NL |  |  |  | RL Amperage |  | 5.13
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.29"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.098"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.388"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.33
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F43-1 | LIVING | SR | 10 | 305 | 260 | 260 | 0.85246 | Unit only rated for 1500 CFM based on submitals
F43-2 | LIVING | SR | 10 | 310 | 225 | 225 | 0.72581
F43-3 | LIVING | SR | 10 | 305 | 228 | 228 | 0.74754
F43-4 | BED | SR | 10 | 275 | 232 | 232 | 0.84364
F43-5 | BED | SR | 10 | 270 | 229 | 229 | 0.84815
F43-6 | BED | SR | 10 | 275 | 238 | 238 | 0.86545
SA TOTAL |  |  |  | 1740 |  | 1412 | 0.81149
R43-1 |  | RR | 22X22 | 1740 | 1487 | 1487 | 0.8546
RA TOTAL |  |  |  | 1740 |  | 1487 | 0.8546
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU04-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU04-4 (FCU-D) |  | Area: 407
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R321R000 |  |  |  | SA CFM | 670 | 695
Serial Num | 356318-6 |  |  |  | Fan Speed |  | HIGH
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 670 | 932
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 3.9
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.16"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.25"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.41"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.2574
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F44-1 | LIVING | SR | 10 | 305 | 249 | 310 | 1.0164
F44-2 | LIVING | SR | 10 | 305 | 277 | 323 | 1.059
F44-3 | LIVING | SR | 10 | 60 | 45 | 62 | 1.0333
SA TOTAL |  |  |  | 670 | 571 | 695 | 1.0373
R44-1 |  | RR | 16X16 | 670 | 577 | 932 | 1.391
RA TOTAL |  |  |  | 670 | 577 | 932 | 1.391
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU04-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU04-5 (FCU-E) |  | Area: 408
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211R000 |  |  |  | SA CFM | 370 | 395
Serial Num | 356318-7 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 370 | 384
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 1.45
Horsepower | 0.33 |  |  |  | Suction ESP |  | 0.31"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.19"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.5"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.095
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F45-1 | LIVING | SR | 10 | 310 | 288 | 288 | 0.92903
F45-2 | LIVING | SR | 10 | 60 | 107 | 107 | 1.7833
SA TOTAL |  |  |  | 370 | 395 | 395 | 1.0676
R45-1 |  | RR | 12X12 | 370 | 384 | 384 | 1.0378
RA TOTAL |  |  |  | 370 | 384 | 384 | 1.0378
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU04-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU04-6 (FCU-B2) |  | Area: 403
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPRO15 |  |  |  | SA CFM | 1740 | 1442
Serial Num | 356318-4 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1532
Motor Data |  |  |  |  | RL Voltage |  | 122.6
Motor MFG | NL |  |  |  | RL Amperage |  | 5.72
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.31"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.094"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.4"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F46-1 | BED | SR | 10 | 275 | 197 | 211 | 0.76727 | Unit only rated for 1500 CFM based on submitals
F46-2 | BED | SR | 10 | 270 | 221 | 218 | 0.80741
F46-3 | BED | SR | 10 | 275 | 180 | 191 | 0.69455
F46-4 | LIVING | SR | 10 | 305 | 326 | 287 | 0.94098
F46-5 | LIVING | SR | 10 | 305 | 252 | 271 | 0.88852
F46-6 | LIVING | SR | 10 | 310 | 251 | 264 | 0.85161
SA TOTAL |  |  |  | 1740 |  | 1442 | 0.82874
R46-1 |  | RR | 24X24 | 1740 | 1532 | 1532 | 0.88046
RA TOTAL |  |  |  | 1740 |  | 1532 | 0.88046
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU04-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU04-7 (FCU-F) |  | Area: 410
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Filter is clogged and removed for testing. Prelim CFM is with dirty filter. Final CFM with filter Removed.
Model Num | HPPR008W4R421R000 |  |  |  | SA CFM | 780 | 787
Serial Num | 356318-8 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 780 | 787
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NA |  |  |  | RL Amperage |  | 3.9
Horsepower | 0.33 |  |  |  | Suction ESP |  | 0.09"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.19"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.28"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.257
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F47-1 | BED | SR | 10 | 230 | 105 | 248 | 1.0783
F47-2 | LIVING | SR | 10 | 180 | 115 | 182 | 1.0111
F47-3 | LIVING | SR | 10 | 185 | 123 | 169 | 0.91351
F47-4 | LIVING | SR | 10 | 185 | 109 | 188 | 1.0162
SA TOTAL |  |  |  | 780 | 452 | 787 | 1.009
R47-1 |  | RR | 16X16 | 780 | 427 | 787 | 1.009
RA TOTAL |  |  |  | 780 | 427 | 787 | 1.009
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU04-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU04-8 (FCU-LOBBY) |  | Area: 419
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006 |  |  |  | SA CFM | 370 | 391
Serial Num | 356318-9 |  |  |  | Fan RPM |  | MED
[5 empty] | OA CFM | 0 | NA
[5 empty] | RA CFM | 200 | 391
Motor Data |  |  |  |  | RL Voltage |  | 120
Motor MFG | NA |  |  |  | RL Amperage |  | 2
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.77
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.11
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.88
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.13
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F48-1 | 519 | CD-1 |  | 200 | 321 | 213 | 1.065
F48-2 | 518 | SR-Z |  | 110 | 150 | 115 | 1.0455
F48-3 | 517 | SR-ZA |  | 60 | 130 | 63 | 1.05
SA TOTAL |  |  |  | 370 | 601 | 391 | 1.0568
R48-1 | 519 | RR-9 | 8 | 200 | 601 | 391 | 1.955
RA TOTAL |  |  |  | 200 |  | 391 | 1.955
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU04-9
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU04-9 (FCU-A2) |  | Area: 404
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Supply and return grills missing.
Model Num |  |  |  |  | SA CFM | 2430
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 0
[5 empty] | RA CFM | 2430
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP | 0.4
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F49-1 | BED | SR | 10 | 255 |  |  | 0
F49-2 | BED | SR | 10 | 255 |  |  | 0
F49-3 | LIVING | SR | 10 | 320 |  |  | 0
F49-4 | LIVING | SR | 10 | 320 |  |  | 0
F49-5 | LIVING | SR | 10 | 320 |  |  | 0
F49-6 | LIVING | SR | 10 | 320 |  |  | 0
F49-7 | LIVING | SR | 10 | 320 |  |  | 0
F49-8 | LIVING | SR | 10 | 320 |  |  | 0
SA TOTAL |  |  |  | 2430 |  | 0 | 0
R49-1 |  | RR | 30X30 | 2430 |  |  | 0
RA TOTAL |  |  |  | 2430 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU05-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU05-1 (FCU-G1) |  | Area: 505
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022 |  |  |  | SA CFM | 2580 | 1833 | HIGH FAN SPEED SETPOINT
Serial Num | 356318-1 |  |  |  | Fan Speed |  | High | Unit only rated for 2200 CFM based on submitals
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2580 | 1833
Motor Data |  |  |  |  | RL Voltage |  | NA
Motor MFG | NA |  |  |  | RL Amperage |  | NA
Horsepower | 0.5 |  |  |  | Suction ESP |  | NA
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.30"
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F51-1 | BED 1 | SR | 10 | 380 | 261 | 261 | 0.68684
F51-2 | BED 2 | SR | 10 | 300 | 203 | 203 | 0.67667
F51-3 | BED 2 | SR | 10 | 300 | 202 | 202 | 0.67333
F51-4 | LIVING | SR | 10 | 320 | 229 | 229 | 0.71562
F51-5 | LIVING | SR | 10 | 320 | 236 | 236 | 0.7375
F51-6 | LIVING | SR | 10 | 320 | 234 | 234 | 0.73125
F51-7 | LIVING | SR | 10 | 320 | 232 | 232 | 0.725
F51-8 | LIVING | SR | 10 | 320 | 236 | 236 | 0.7375
SA TOTAL |  |  |  | 2580 | 1833 | 1833 | 0.71047
R51-1 |  | RR | 28X28 | 2580 | 1833 | 1833
RA TOTAL |  |  |  | 2580 | 1833 | 1833 | 0.71047
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU05-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU05-2 (FCU-Q) |  | Area: 501
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008 |  |  |  | SA CFM | 990 | 982 |  | LOW SPEED SETPOINT
Serial Num | 356318-5 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | NA
[5 empty] | RA CFM | 990 | 982
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NA |  |  |  | RL Amperage |  | 1.9
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.03" | PRESSURE TAKEN FROM RETURN DUCT
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.08" | PRESSURE TAKEN FROM SUPPLY DUCT
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.11"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F52-1 | STUDIO | SR | 10 | 330 | 309 | 302 | 0.92
F52-2 | STUDIO | SR | 10 | 330 | 325 | 324 | 0.98
F52-3 | STUDIO | SR | 10 | 330 | 426 | 356 | 1.08
SA TOTAL |  |  |  | 990 | 1060 | 982 | 0.99
R52-1 |  | RR | 18X18 | 990 | 1060 | 982 | 0.99
RA TOTAL |  |  |  | 990 |  | 982 | 0.99
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU05-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU05-3 (FCU-B1) |  | Area: 502
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR015W4R411L000 |  |  |  | SA CFM | 1740 | 1428 | High speed setpoint
Serial Num | 356318-3 |  |  |  | Fan Speed |  | High | Unit undersized, based on submitals unit is only capable of 1500 CFM
[5 empty] | OA CFM | 0 | 0 | Balanced proportionaly
[5 empty] | RA CFM | 1740 | 1428 | Amperage is for both motors at the same time.
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 5.5
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.33"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.12"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.45"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.363
Amperage (rated) | 5
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F53-1 | LIVING | SR | 10 | 305 | 255 | 255 | 0.83607
F53-2 | LIVING | SR | 10 | 310 | 257 | 257 | 0.82903
F53-3 | LIVING | SR | 10 | 305 | 245 | 245 | 0.80328
F53-4 | BED | SR | 10 | 275 | 236 | 236 | 0.85818
F53-5 | BED | SR | 10 | 270 | 211 | 211 | 0.78148
F53-6 | BED | SR | 10 | 275 | 224 | 224 | 0.81455
SA TOTAL |  |  |  | 1740 | 1428 | 1428 | 0.82069
R53-1 |  | RR | 22X22 | 1740 | 1428 | 1428 | 0.82069
RA TOTAL |  |  |  | 1740 | 1428 | 1428 | 0.82069
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU05-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU05-4 (FCU-D) |  | Area: 507
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008 |  |  |  | SA CFM | 670 | 717
Serial Num | 356318-6 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 670 | 665
Motor Data |  |  |  |  | RL Voltage |  | 125.3
Motor MFG | NL |  |  |  | RL Amperage |  | 4.76
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.64"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.24"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.68"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Fan speed at highest set pt.
F54-1 | LIVING | SR | 10 | 305 | 301 | 320 | 1.0492 | Diffuser 3 above design, face damper fully closed.
F54-2 | LIVING | SR | 10 | 305 | 292 | 327 | 1.0721
F54-3 | LIVING | SR | 10 | 60 | 135 | 70 | 1.1667
SA TOTAL |  |  |  | 670 |  | 717 | 1.0701
R54-1 |  | RR | 16X16 | 670 | 665 | 665 | 0.99254
RA TOTAL |  |  |  | 670 |  | 665 | 0.99254
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU05-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU05-5 (FCU-E) |  | Area: 508
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211R000 |  |  |  | SA CFM | 370 | 374 | LOW SPEED SETPOINT
Serial Num | 356318 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | NA
[5 empty] | RA CFM | 370 | 374
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NA |  |  |  | RL Amperage |  | 0.71
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.06
Motor Rpm | NL |  |  |  | Discharge ESP |  | NA
Phase | 1 |  |  |  | Total ESP | 0.4 | NA
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F55-1 | LIVING | SR | 10 | 310 | 354 | 313 | 1.01
F55-2 | LIVING | SR | 10 | 60 | 34 | 61 | 1.02
SA TOTAL |  |  |  | 370 |  | 374 | 1.01
R55-1 |  | RR | 12X12 | 370 |  | 374 | 1.01
RA TOTAL |  |  |  | 370 |  | 374 | 1.01
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU05-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU05-6 (FCU-B2) |  | Area: 503
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR015W4R411R000 |  |  |  | SA CFM | 1740 | 1563
Serial Num | 356318-4 |  |  |  | Fan Speed |  | HIGH
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1563
Motor Data |  |  |  |  | RL Voltage |  | 122 | HIGH FAN SPEED SETPOINT
Motor MFG | NA |  |  |  | RL Amperage |  | 6.2 | UNABLE TO INDIVIDUALY ISOLATE MOTOR AMPERAGE, LISTED AMPERAGE IS FOR BOTH MOTORS COMBINED.
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.09 | Unit undersized, based on submitals unit is only capable of 1500 CFM
Motor Rpm | NL |  |  |  | Discharge ESP |  | NA
Phase | 1 |  |  |  | Total ESP | 0.4 | NA
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 5
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F56-1 | BED | SR | 10 | 275 | 238 | 238 | 0.86545
F56-2 | BED | SR | 10 | 270 | 243 | 243 | 0.9
F56-3 | BED | SR | 10 | 275 | 252 | 252 | 0.91636
F56-4 | LIVING | SR | 10 | 305 | 282 | 282 | 0.92459
F56-5 | LIVING | SR | 10 | 305 | 276 | 276 | 0.90492
F56-6 | LIVING | SR | 10 | 310 | 272 | 272 | 0.87742
SA TOTAL |  |  |  | 1740 | 1563 | 1563 | 0.89828
R56-1 |  | RR | 24X24 | 1740 | 1563 | 1563 | 0.89
RA TOTAL |  |  |  | 1740 | 1563 | 1764 | 0.89
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU05-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU05-7 (FCU-F) |  | Area: 510
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008 |  |  |  | SA CFM | 780 | 716
Serial Num | 356318-8 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 780 | 711
Motor Data |  |  |  |  | RL Voltage |  | 126.3
Motor MFG | NL |  |  |  | RL Amperage |  | 4.75
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.71"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.14"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.85"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Fan speed set to highest set pt.
F57-1 | BED | SR | 10 | 230 | 164 | 202 | 0.87826
F57-2 | LIVING | SR | 10 | 180 | 180 | 168 | 0.93333
F57-3 | LIVING | SR | 10 | 185 | 193 | 174 | 0.94054
F57-4 | LIVING | SR | 10 | 185 | 181 | 172 | 0.92973
SA TOTAL |  |  |  | 780 |  | 716 | 0.91795
R57-1 |  | RR | 16X16 | 780 | 711 | 711 | 0.91154
RA TOTAL |  |  |  | 780 |  | 711 | 0.91154
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU05-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU05-8 (FCU-LOBBY) |  | Area: 519
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR0 |  |  |  | SA CFM | 370 | 394
Serial Num | 356318- |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 200 | 394
Motor Data |  |  |  |  | RL Voltage |  | 124.2
Motor MFG | NL |  |  |  | RL Amperage |  | 2.44
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.39"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.17"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.56" | . Filters removed for testing
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.16 | . Medium fan speed
Amperage (rated) | 5 | [6 empty] | . Supply air and return air numbers are not compatible with 0 outside air, return damper left full open
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F58-1 | 519 | CD-1 |  | 200 | 261 | 213 | 1.065
F58-2 | 518 | SR-Z |  | 110 | 87 | 118 | 1.0727
F58-3 | 517 | SR-ZA |  | 60 | 78 | 63 | 1.05
SA TOTAL |  |  |  | 370 |  | 394 | 1.0649
R58-1 | 519 | RR-9 | 8 | 200 |  |  | 0
RA TOTAL |  |  |  | 200 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU05-9
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU05-9 (FCU-A2) |  | Area: 504
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022W4R411R |  |  |  | SA CFM | 2430 | 2244
Serial Num | 356318-2 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2430 | 2244
Motor Data |  |  |  |  | RL Voltage |  | 123.2
Motor MFG | NL |  |  |  | RL Amperage |  | 12.56
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.29"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.36"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.65"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.4 | . Two fan motors
Amperage (rated) | 7.7 | [6 empty] | . High fan speed
. Filter removed for testing
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F59-1 | BED | SR | 10 | 255 | 387 | 262 | 1.0275
F59-2 | BED | SR | 10 | 255 | 392 | 254 | 0.99608
F59-3 | LIVING | SR | 10 | 320 | 229 | 257 | 0.80312
F59-4 | LIVING | SR | 10 | 320 | 256 | 271 | 0.84688
F59-5 | LIVING | SR | 10 | 320 | 261 | 283 | 0.88438
F59-6 | LIVING | SR | 10 | 320 | 272 | 293 | 0.91563
F59-7 | LIVING | SR | 10 | 320 | 289 | 315 | 0.98438
F59-8 | LIVING | SR | 10 | 320 | 271 | 309 | 0.96562
SA TOTAL |  |  |  | 2430 |  | 2244 | 0.92346
R59-1 |  | RR | 30X30 | 2430 |  |  | 0
RA TOTAL |  |  |  | 2430 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU06-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU06-1 (FCU-G1) |  | Area: 605
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022 |  |  |  | SA CFM | 2580 | 1971 | Notes
Serial Num | 356318-1 |  |  |  | Fan Speed |  | High | Not enough wires were ran to the thermostat from the fan coil for 3 speed, configured thermostat for 2 speed high and low
[5 empty] | OA CFM | 0 | 0 | Amperage is for both motors at the same time.
[5 empty] | RA CFM | 2580 | 1971 | High speed setpoint
Motor Data |  |  |  |  | RL Voltage |  | 123 | Unit only rated for 2200 CFM based on submitals
Motor MFG | NA |  |  |  | RL Amperage |  | 13.5
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.09"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.14"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.23"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.876
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F61-1 | BED 1 | SR | 10 | 380 | 305 | 305 | 0.80263
F61-2 | BED 2 | SR | 10 | 300 | 236 | 236 | 0.78667
F61-3 | BED 2 | SR | 10 | 300 | 228 | 228 | 0.76
F61-4 | LIVING | SR | 10 | 320 | 241 | 241 | 0.75313
F61-5 | LIVING | SR | 10 | 320 | 255 | 255 | 0.79688
F61-6 | LIVING | SR | 10 | 320 | 224 | 224 | 0.7
F61-7 | LIVING | SR | 10 | 320 | 232 | 232 | 0.725
F61-8 | LIVING | SR | 10 | 320 | 250 | 250 | 0.78125
SA TOTAL |  |  |  | 2580 | 1971 | 1971 | 0.76395
R61-1 |  | RR | 28X28 | 2580 | 1971 | 1971
RA TOTAL |  |  |  | 2580 | 1971 | 1971 | 0.763
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU06-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU06-2 (FCU-Q) |  | Area: 601
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | NOTES
Model Num | HPPR008 |  |  |  | SA CFM | 990 | 987 | Medium speed setpoint
Serial Num | 356318-5 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | NA
[5 empty] | RA CFM | 990 | 987
Motor Data |  |  |  |  | RL Voltage |  | 125
Motor MFG | NA |  |  |  | RL Amperage |  | 4.05
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.06"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.1"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.16"
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F62-1 | STUDIO | SR | 10 | 330 | 339 | 353 | 1.07
F62-2 | STUDIO | SR | 10 | 330 | 309 | 316 | 0.96
F62-3 | STUDIO | SR | 10 | 330 | 368 | 318 | 0.96
SA TOTAL |  |  |  | 990 | 1016 | 987 | 1
R62-1 |  | RR | 18X18 | 990 | 1016 | 987 | 1
RA TOTAL |  |  |  | 990 |  | 987 | 1
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU06-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU06-3 (FCU-B1) |  | Area: 602
Unit Data |  |  |  |  | Test Data |  |  | NOTES
MFG | WHALEN |  |  |  |  | Design | Actual | High speed setpoint
Model Num | HPPR015W4R411L000 |  |  |  | SA CFM | 1740 | 1388 | Amperage for both motors at the same time.
Serial Num | 356318-3 |  |  |  | Fan Speed |  | High | Unit only rated for 1500 CFM based on submitals
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1388
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NA |  |  |  | RL Amperage |  | 7.3
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.08"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.12"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.20"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.481
Amperage (rated) | 5
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F63-1 | LIVING | SR | 10 | 305 | 248 | 248 | 0.81311
F63-2 | LIVING | SR | 10 | 310 | 236 | 236 | 0.76129
F63-3 | LIVING | SR | 10 | 305 | 254 | 254 | 0.83279
F63-4 | BED | SR | 10 | 275 | 234 | 234 | 0.85091
F63-5 | BED | SR | 10 | 270 | 210 | 210 | 0.77778
F63-6 | BED | SR | 10 | 275 | 206 | 206 | 0.74909
SA TOTAL |  |  |  | 1740 | 1388 | 1388 | 0.7977
R63-1 |  | RR | 22X22 | 1740 | 1388 | 1388 | 0.7977
RA TOTAL |  |  |  | 1740 | 1388 | 1388 | 0.7977
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU06-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU06-4 (FCU-D) |  | Area: 607
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008 |  |  |  | SA CFM | 670 | 720
Serial Num | 356318-6 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 670 | 698
Motor Data |  |  |  |  | RL Voltage |  | 123.6
Motor MFG | NL |  |  |  | RL Amperage |  | 4.87
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.73"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.32"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.95"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Fan speed at highest set pt.
F64-1 | LIVING | SR | 10 | 305 | 317 | 309 | 1.0131 | Diffuser 3 above design, face damper fully closed.
F64-2 | LIVING | SR | 10 | 305 | 383 | 322 | 1.0557
F64-3 | LIVING | SR | 10 | 60 | 184 | 89 | 1.4833
SA TOTAL |  |  |  | 670 |  | 720 | 1.0746
R64-1 |  | RR | 16X16 | 670 | 698 | 698 | 1.0418
RA TOTAL |  |  |  | 670 |  | 698 | 1.0418
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU06-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU06-5 (FCU-E) |  | Area: 608
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R11R000 |  |  |  | SA CFM | 370 | 411 | NOTES
Serial Num | 356318-7 |  |  |  | Fan RPM |  | NA | MEDIUM SPEED SETPOINT
[5 empty] | OA CFM | 0 | NA | BEDROOM DIFFUSER DAMPER FULLY CLOSED AND ABOVE DESIGN
[5 empty] | RA CFM | 370 | 411 | MEDIUM SPEED SELECTED DUE TO LOW SPEED BEING 80% OF DESIGN PRIOR TO BALANCING
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NA |  |  |  | RL Amperage |  | 1.4
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.15
Motor Rpm | NA |  |  |  | Discharge ESP |  | NA
Phase | 1 |  |  |  | Total ESP | 0.4 | NA
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F65-1 | LIVING | SR | 10 | 310 | 159 | 339 | 1.09
F65-2 | LIVING | SR | 10 | 60 | 141 | 72 | 1.2
SA TOTAL |  |  |  | 370 | 300 | 411 | 1.11
R65-1 |  | RR | 12X12 | 370 |  | 411 | 1.11
RA TOTAL |  |  |  | 370 |  | 411 | 1.11
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU06-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU06-6 (FCU-B2) |  | Area: 603
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR015W4R411R000 |  |  |  | SA CFM | 1740 | 1440
Serial Num | 356318-4 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1440 | Notes:
Motor Data |  |  |  |  | RL Voltage |  | 122 | High speed setpoint
Motor MFG | NA |  |  |  | RL Amperage |  | 5.9 | Amperage for both motors at the same time.
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.06" | Unit only capable of 1500 CFM based on submitals.
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.07"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.13"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.389
Amperage (rated) | 5
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F66-1 | BED | SR | 10 | 275 | 211 | 211 | 0.76727
F66-2 | BED | SR | 10 | 270 | 214 | 214 | 0.79259
F66-3 | BED | SR | 10 | 275 | 231 | 231 | 0.84
F66-4 | LIVING | SR | 10 | 305 | 267 | 267 | 0.87541
F66-5 | LIVING | SR | 10 | 305 | 261 | 261 | 0.85574
F66-6 | LIVING | SR | 10 | 310 | 256 | 256 | 0.82581
SA TOTAL |  |  |  | 1740 | 1440 | 1440 | 0.82759
R66-1 |  | RR | 24X24 | 1740 | 1440 | 1440 | 0.82759
RA TOTAL |  |  |  | 1740 | 1440 | 1440 | 0.82759
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU06-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU06-7 (FCU-F) |  | Area: 610
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R421R000 |  |  |  | SA CFM | 780 | 789
Serial Num | 356318-8 |  |  |  | Fan RPM |  | NA | Medium speed setpoint
[5 empty] | OA CFM | 0 | NA
[5 empty] | RA CFM | 780 | 789
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NA |  |  |  | RL Amperage |  | 2.6
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.09"
Motor Rpm | NA |  |  |  | Discharge ESP |  | NA
Phase | 1 |  |  |  | Total ESP | 0.4 | NA
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F67-1 | BED | SR | 10 | 230 | 187 | 236 | 1.03
F67-2 | LIVING | SR | 10 | 180 | 189 | 180 | 1
F67-3 | LIVING | SR | 10 | 185 | 250 | 190 | 1.03
F67-4 | LIVING | SR | 10 | 185 | 224 | 183 | 0.99
SA TOTAL |  |  |  | 780 | 850 | 789 | 1.01
R67-1 |  | RR | 16X16 | 780 | 850 | 789 | 1.01
RA TOTAL |  |  |  | 780 |  | 789 | 1.01
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU06-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU06-8 (FCU-LOBBY) |  | Area: 619
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211L |  |  |  | SA CFM | 370 | 372
Serial Num | 356318-9 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 200 | 368
Motor Data |  |  |  |  | RL Voltage |  | 125.4
Motor MFG | NL |  |  |  | RL Amperage |  | 1.78 | . Filters dirty, removed for testing
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.36" | . Medium Fan speed
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.26 | . Supply air and return air numbers are not compatible with 0 outside air, return damper left full open
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.62
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.11
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F68-1 | 619 | CD-1 |  | 200 | 193 | 193 | 0.965
F68-2 | 618 | SR-Z |  | 110 | 123 | 114 | 1.0364
F68-3 | 617 | SR-ZA |  | 60 | 78 | 65 | 1.0833
SA TOTAL |  |  |  | 370 |  | 372 | 1.0054
R68-1 | 619 | RR-9 | 8 | 200 |  | 368 | 1.84
RA TOTAL |  |  |  | 200 |  | 368 | 1.84
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU06-9
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU06-9 (FCU-A2) |  | Area: 604
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | . Filters removed for testing
Model Num | HPPR022W4R411R |  |  |  | SA CFM | 2430 | 2282 | . Unit in high speed
Serial Num | 356318-2 |  |  |  | Fan RPM |  | NA | . Unit has two motors, amperage reflects them both
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2430 | 2209
Motor Data |  |  |  |  | RL Voltage |  | 123.4
Motor MFG | NL |  |  |  | RL Amperage |  | 13.25
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.54
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.49"
Phase | 1 |  |  |  | Total ESP | 0.4 | 1.03
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.42
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F69-1 | BED | SR | 10 | 255 | 400 | 266 | 1.0431
F69-2 | BED | SR | 10 | 255 | 353 | 231 | 0.90588
F69-3 | LIVING | SR | 10 | 320 | 215 | 253 | 0.79063
F69-4 | LIVING | SR | 10 | 320 | 290 | 300 | 0.9375
F69-5 | LIVING | SR | 10 | 320 | 276 | 306 | 0.95625
F69-6 | LIVING | SR | 10 | 320 | 261 | 313 | 0.97813
F69-7 | LIVING | SR | 10 | 320 | 234 | 282 | 0.88125
F69-8 | LIVING | SR | 10 | 320 | 315 | 331 | 1.0344
SA TOTAL |  |  |  | 2430 |  | 2282 | 0.93909
R69-1 |  | RR | 30X30 | 2430 | 2187 | 2209 | 0.90905
RA TOTAL |  |  |  | 2430 |  | 2209 | 0.90905
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU07-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU07-1 (FCU-G1) |  | Area: 705
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022 |  |  |  | SA CFM | 2580 | 1848
Serial Num | 356318-1 |  |  |  | Fan Speed |  | High | Unit unable to meet design; unit undersized per submitals. Unit is only capable of 2200 CFM per submitals. Unit balanced proportionally. Heat does not work at this time 11/21/2024. Amperage is for both motors at the same time.
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2580 | 1848
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 12.4
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.10"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.13"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.23"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.805
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F71-1 | BED 1 | SR | 10 | 380 | 230 | 279 | 0.73421
F71-2 | BED 2 | SR | 10 | 300 | 245 | 210 | 0.7
F71-3 | BED 2 | SR | 10 | 300 | 234 | 223 | 0.74333
F71-4 | LIVING | SR | 10 | 320 | 236 | 238 | 0.74375
F71-5 | LIVING | SR | 10 | 320 | 210 | 227 | 0.70937
F71-6 | LIVING | SR | 10 | 320 | 273 | 218 | 0.68125
F71-7 | LIVING | SR | 10 | 320 | 224 | 241 | 0.75313
F71-8 | LIVING | SR | 10 | 320 | 245 | 212 | 0.6625
SA TOTAL |  |  |  | 2580 | 1897 | 1848 | 0.71628
R71-1 |  | RR | 28X28 | 2580 | 1848 | 1848 | 0.72
RA TOTAL |  |  |  | 2580 | 1848 | 1848 | 0.71628
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU07-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU07-2 (FCU-Q) |  | Area: 701
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR010 |  |  |  | SA CFM | 990 | 925
Serial Num | 356318-5 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 990 | 911
Motor Data |  |  |  |  | RL Voltage |  | 122.3
Motor MFG | NL |  |  |  | RL Amperage |  | 7.21
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.51"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.20"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.71"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Fan speed at highest set pt.
F72-1 | STUDIO | SR | 10 | 330 | 317 | 308 | 0.93333
F72-2 | STUDIO | SR | 10 | 330 | 322 | 315 | 0.95455
F72-3 | STUDIO | SR | 10 | 330 | 280 | 302 | 0.91515
SA TOTAL |  |  |  | 990 |  | 925 | 0.93434
R72-1 |  | RR | 18X18 | 990 | 911 | 911 | 0.9202
RA TOTAL |  |  |  | 990 |  | 911 | 0.9202
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU07-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU07-3 (FCU-B1) |  | Area: 702
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR015W4R411L000 |  |  |  | SA CFM | 1740 | 1369 | Notes:
Serial Num | 356318-3 |  |  |  | Fan Speed |  | High | High speed setpoint
[5 empty] | OA CFM | 0 | 0 | Unit only capable of 1500 CFM per submitals
[5 empty] | RA CFM | 1740 | 1369
Motor Data |  |  |  |  | RL Voltage |  | 123
Motor MFG | NA |  |  |  | RL Amperage |  | 3.8
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.04
Motor Rpm | NL |  |  |  | Discharge ESP |  | NA
Phase | 1 |  |  |  | Total ESP | 0.4 | NA
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated) | 5
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F73-1 | LIVING | SR | 10 | 305 | 238 | 238 | 0.78033
F73-2 | LIVING | SR | 10 | 310 | 255 | 255 | 0.82258
F73-3 | LIVING | SR | 10 | 305 | 243 | 243 | 0.79672
F73-4 | BED | SR | 10 | 275 | 227 | 227 | 0.82545
F73-5 | BED | SR | 10 | 270 | 205 | 205 | 0.75926
F73-6 | BED | SR | 10 | 275 | 201 | 201 | 0.73091
SA TOTAL |  |  |  | 1740 | 1369 | 1369 | 0.78678
R73-1 |  | RR | 22X22 | 1740 | 1369 | 1369 | 0.78678
RA TOTAL |  |  |  | 1740 | 1369 | 1369 | 0.78678
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU07-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU07-4 (FCU-D) |  | Area: 707
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R321R000 |  |  |  | SA CFM | 670 | 628
Serial Num | 356318-6 |  |  |  | Fan Speed |  | MEDIUM
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 670 | 628
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 2.5
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.11
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.11"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.22"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.165
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F74-1 | LIVING | SR | 10 | 305 | 281 | 281 | 0.92131
F74-2 | LIVING | SR | 10 | 305 | 289 | 289 | 0.94754
F74-3 | LIVING | SR | 10 | 60 | 58 | 58 | 0.96667
SA TOTAL |  |  |  | 670 | 628 | 628 | 0.93731
R74-1 |  | RR | 16X16 | 670 | 628 | 628 | 0.93731
RA TOTAL |  |  |  | 670 | 628 | 628 | 0.93731
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU07-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU07-5 (FCU-E) |  | Area: 708
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211R000 |  |  |  | SA CFM | 370 | 376 | NOTES
Serial Num | 356318-7 |  |  |  | Fan RPM |  | NA | LOW SPEED SETPOINT
[5 empty] | OA CFM | 0 | NA | DIFFUSER 2 WITH DAMPER FULLY CLOSED EXCEDES DESIGN CFM
[5 empty] | RA CFM | 370 | 376
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NA |  |  |  | RL Amperage |  | 0.85
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.06
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.07
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.13"
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F75-1 | LIVING | SR | 10 | 310 | 214 | 306 | 0.99
F75-2 | LIVING | SR | 10 | 60 | 149 | 70 | 1.17
SA TOTAL |  |  |  | 370 | 363 | 376 | 1.02
R75-1 |  | RR | 12X12 | 370 |  | 376 | 1.02
RA TOTAL |  |  |  | 370 | 363 | 376 | 1.02
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU07-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU07-6 (FCU-B2) |  | Area: 703
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR015W4R411R000 |  |  |  | SA CFM | 1740 | 1512 | NOTES
Serial Num | 356318-4 |  |  |  | Fan RPM |  | NA | HIGH SPEED SETPOINT
[5 empty] | OA CFM | 0 | 0 | Unit only rated for 1500 CFM
[5 empty] | RA CFM | 1740 | 1512 | Unit balanced proportionally
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NA |  |  |  | RL Amperage |  | 7
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.10"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.14"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.24"
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated) | 5
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F76-1 | BED | SR | 10 | 275 | 234 | 234 | 0.85
F76-2 | BED | SR | 10 | 270 | 243 | 243 | 0.9
F76-3 | BED | SR | 10 | 275 | 233 | 233 | 0.84
F76-4 | LIVING | SR | 10 | 305 | 266 | 266 | 0.87
F76-5 | LIVING | SR | 10 | 305 | 272 | 272 | 0.89
F76-6 | LIVING | SR | 10 | 310 | 264 | 264 | 0.85
SA TOTAL |  |  |  | 1740 | 1512 | 1512 | 0.86
R76-1 |  | RR | 24X24 | 1740 | 1512 | 1512 | 0.86
RA TOTAL |  |  |  | 1740 | 1512 | 1512 | 0.86
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU07-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU07-7 (FCU-F) |  | Area: 710
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008 |  |  |  | SA CFM | 780 | 766
Serial Num | 356318-8 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 780 | 742
Motor Data |  |  |  |  | RL Voltage |  | 124.7
Motor MFG | NL |  |  |  | RL Amperage |  | 4.89
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.58"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.13"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.71"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Fan speed at highest set pt.
F77-1 | BED | SR | 10 | 230 | 214 | 214 | 0.93043
F77-2 | LIVING | SR | 10 | 180 | 178 | 178 | 0.98889
F77-3 | LIVING | SR | 10 | 185 | 182 | 182 | 0.98378
F77-4 | LIVING | SR | 10 | 185 | 192 | 192 | 1.0378
SA TOTAL |  |  |  | 780 |  | 766 | 0.98205
R77-1 |  | RR | 16X16 | 780 | 742 | 742 | 0.95128
RA TOTAL |  |  |  | 780 |  | 742 | 0.95128
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU07-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU07-8 (FCU-LOBBY) |  | Area: 719
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211 |  |  |  | SA CFM | 370 | 406
Serial Num | 356318-9 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 200 | 406
Motor Data |  |  |  |  | RL Voltage |  | 123.5
Motor MFG | NL |  |  |  | RL Amperage |  | 1.76
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.46"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.13"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.59"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.11
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | . Diffuser 1 missing damper
F78-1 | 719 | CD-1 |  | 200 | 238 | 238 | 1.19 | . Medium fan speed
F78-2 | 718 | SR-Z |  | 110 | 132 | 105 | 0.95455 | . Supply air and return air numbers are not compatible with 0 outside air, return damper left full open
F78-3 | 717 | SR-ZA |  | 60 | 87 | 63 | 1.05
SA TOTAL |  |  |  | 370 |  | 406 | 1.0973
R78-1 | 719 | RR-9 | 8 | 200 |  | 406 | 2.03
RA TOTAL |  |  |  | 200 |  | 406 | 2.03
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU07-9
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU07-9 (FCU-A2) |  | Area: 704
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022W4R411R |  |  |  | SA CFM | 2430 | 2270
Serial Num | 356318-2 |  |  |  | Fan RPM |  | NA | Notes: Amperage is for both motors at the same time. Unit only rated for 2200 CFM per submitals.
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2430 | 2270
Motor Data |  |  |  |  | RL Voltage |  | 122.8
Motor MFG | NL |  |  |  | RL Amperage |  | 12.52
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.35"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.17"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.52"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.4
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F89-1 | BED | SR | 10 | 255 | 316 | 258 | 1.0118
F89-2 | BED | SR | 10 | 255 | 343 | 243 | 0.95294
F89-3 | LIVING | SR | 10 | 320 | 261 | 249 | 0.77812
F89-4 | LIVING | SR | 10 | 320 | 262 | 315 | 0.98438
F89-5 | LIVING | SR | 10 | 320 | 233 | 274 | 0.85625
F89-6 | LIVING | SR | 10 | 320 | 289 | 314 | 0.98125
F89-7 | LIVING | SR | 10 | 320 | 298 | 322 | 1.0063
F89-8 | LIVING | SR | 10 | 320 | 269 | 295 | 0.92188
SA TOTAL |  |  |  | 2430 | 2271 | 2270 | 0.93416
R89-1 |  | RR | 30X30 | 2430 |  |  | 0
RA TOTAL |  |  |  | 2430 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU08-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU08-1 (FCU-G1) |  | Area: 805
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Unit only rated for 2200 CFM per submitals. unit balanced proportionally. Amperage is for both motors at the same time.
Model Num | HPPR022 |  |  |  | SA CFM | 2580 | 2011
Serial Num | 356318-1 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2580 | 2011
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 13.2
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.11"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.14"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.25"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.857
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F81-1 | BED 1 | SR | 10 | 380 | 281 | 281 | 0.73947
F81-2 | BED 2 | SR | 10 | 300 | 245 | 245 | 0.81667
F81-3 | BED 2 | SR | 10 | 300 | 226 | 226 | 0.75333
F81-4 | LIVING | SR | 10 | 320 | 230 | 230 | 0.71875
F81-5 | LIVING | SR | 10 | 320 | 260 | 260 | 0.8125
F81-6 | LIVING | SR | 10 | 320 | 273 | 273 | 0.85313
F81-7 | LIVING | SR | 10 | 320 | 233 | 233 | 0.72813
F81-8 | LIVING | SR | 10 | 320 | 263 | 263 | 0.82188
SA TOTAL |  |  |  | 2580 | 2011 | 2011 | 0.77946
R81-1 |  | RR | 28X28 | 2580 | 2011 | 2011 | 0.78
RA TOTAL |  |  |  | 2580 | 2011 | 2011 | 0.77946
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU08-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU08-2 (FCU-Q) |  | Area: 801
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR010 |  |  |  | SA CFM | 990 | 1060
Serial Num | 356315-5 |  |  |  | Fan RPM |  | NA | NOTE: MED FANSPEED
[5 empty] | OA CFM | 0 | 0 | GM
[5 empty] | RA CFM | 990 | 1060
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | GENTEQ |  |  |  | RL Amperage |  | 3.5
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.32
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.2
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.52
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F82-1 | STUDIO | SR | 10 | 330 | 459 | 362 | 1.097
F82-2 | STUDIO | SR | 10 | 330 | 423 | 353 | 1.0697
F82-3 | STUDIO | SR | 10 | 330 | 524 | 345 | 1.0455
SA TOTAL |  |  |  | 990 | 1406 | 1060 | 1.0707
R82-1 |  | RR | 18X18 | 990 |  | 1060 | 1.0707
RA TOTAL |  |  |  | 990 |  | 1060 | 1.0707
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU08-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU08-3 (FCU-B1) |  | Area: 802
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes
Model Num | HPPR015W4R411L000 |  |  |  | SA CFM | 1740 | 1375 | Amps read from both fan motors
Serial Num | 356318-3 |  |  |  | Fan Speed |  | High | Fan speed high
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1375
Motor Data |  |  |  |  | RL Voltage |  | 121.8
Motor MFG | NA |  |  |  | RL Amperage |  | 6.63
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.25"
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.14"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.39"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.43
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F83-1 | LIVING | SR | 10 | 305 | 242 | 242 | 0.79344
F83-2 | LIVING | SR | 10 | 310 | 249 | 249 | 0.80323
F83-3 | LIVING | SR | 10 | 305 | 243 | 243 | 0.79672
F83-4 | BED | SR | 10 | 275 | 222 | 222 | 0.80727
F83-5 | BED | SR | 10 | 270 | 208 | 208 | 0.77037
F83-6 | BED | SR | 10 | 275 | 211 | 211 | 0.76727
SA TOTAL |  |  |  | 1740 | 1375 | 1375 | 0.79023
R83-1 |  | RR | 22X22 | 1740 | 1375 | 1376 | 0.7908
RA TOTAL |  |  |  | 1740 | 1375 | 1375 | 0.79023
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU08-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU08-4 (FCU-D) |  | Area: 807
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R321R000 |  |  |  | SA CFM | 670 | 698 | Notes
Serial Num | 356318-6 |  |  |  | Fan RPM |  | NA | Fan speed medium
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 670 | 698
Motor Data |  |  |  |  | RL Voltage |  | 122.2
Motor MFG | NA |  |  |  | RL Amperage |  | 3.05
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.43"
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.24"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.67"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.2
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F84-1 | LIVING | SR | 10 | 305 | 262 | 325 | 1.0656
F84-2 | LIVING | SR | 10 | 305 | 272 | 311 | 1.0197
F84-3 | LIVING | SR | 10 | 60 | 220 | 62 | 1.0333
SA TOTAL |  |  |  | 670 |  | 698 | 1.0418
R84-1 |  | RR | 16X16 | 670 |  | 698 | 1.0418
RA TOTAL |  |  |  | 670 |  | 698 | 1.0418
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU08-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU08-5 (FCU-E) |  | Area: 808
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211R000 |  |  |  | SA CFM | 370 | 360 | Notes
Serial Num | 356318-7 |  |  |  | Fan RPM |  | NA | Fan speed low
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 370 | 360
Motor Data |  |  |  |  | RL Voltage |  | 121.5
Motor MFG | NA |  |  |  | RL Amperage |  | 1.87
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.20"
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.05"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.25"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.05
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F85-1 | LIVING | SR | 10 | 310 | 347 | 295 | 0.95161
F85-2 | LIVING | SR | 10 | 60 | 110 | 65 | 1.0833
SA TOTAL |  |  |  | 370 |  | 360 | 0.97297
R85-1 |  | RR | 12X12 | 370 |  | 360 | 0.97297
RA TOTAL |  |  |  | 370 |  | 360 | 0.97297
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU08-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU08-6 (FCU-B2) |  | Area: 803
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | NOTE: HIGH FANSPEED
Model Num | HPPR015 |  |  |  | SA CFM | 1740 | 1365 | AMPS FROM BOTH MOTORS ADDED
Serial Num | 356318-4 |  |  |  | Fan RPM |  | High | Unit only capable of 1500 CFM per submitals
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1365
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | GENTEQ |  |  |  | RL Amperage |  | 4.9
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.22
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.1
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.32
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.323
Amperage (rated) | 5
QTY | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F86-1 | BED | SR | 10 | 275 | 218 | 218 | 0.79273
F86-2 | BED | SR | 10 | 270 | 224 | 224 | 0.82963
F86-3 | BED | SR | 10 | 275 | 222 | 222 | 0.80727
F86-4 | LIVING | SR | 10 | 305 | 220 | 220 | 0.72131
F86-5 | LIVING | SR | 10 | 305 | 239 | 239 | 0.78361
F86-6 | LIVING | SR | 10 | 310 | 242 | 242 | 0.78065
SA TOTAL |  |  |  | 1740 | 1365 | 1365 | 0.78448
R86-1 |  | RR | 24X24 | 1740 | 1365 | 1365 | 0.78448
RA TOTAL |  |  |  | 1740 | 1365 | 1365 | 0.78448
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU08-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU08-7 (FCU-F) |  | Area: 810
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R421R000 |  |  |  | SA CFM | 780 | 736 | Notes
Serial Num | 356318-8 |  |  |  | Fan RPM |  | NA | Low fan speed
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 780 | 736
Motor Data |  |  |  |  | RL Voltage |  | NA
Motor MFG | NA |  |  |  | RL Amperage |  | 1.38
Horsepower |  |  |  |  | Suction ESP |  | -0.25"
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.036"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.61"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.09
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F87-1 | BED | SR | 10 | 230 | 382 | 210 | 0.91304
F87-2 | LIVING | SR | 10 | 180 | 367 | 168 | 0.93333
F87-3 | LIVING | SR | 10 | 185 | 209 | 176 | 0.95135
F87-4 | LIVING | SR | 10 | 185 | 333 | 182 | 0.98378
SA TOTAL |  |  |  | 780 |  | 736 | 0.94359
R87-1 |  | RR | 16X16 | 780 |  |  | 0
RA TOTAL |  |  |  | 780 |  | 736 | 0.94359
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU08-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU08-8 (FCU-LOBBY) |  | Area: 819
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211L000 |  |  |  | SA CFM | 370 | 412 | Notes: Filters clogged; removed for testing. . Supply air and return air numbers are not compatible with 0 outside air, return damper left full open
Serial Num | 356318-9 |  |  |  | Fan Speed |  | MEDIUM
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 200 | 412
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 1.9
Horsepower | 0.33 |  |  |  | Suction ESP |  | 0.57"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.22"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.79"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 1.15
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F88-1 | 819 | CD-1 |  | 200 | 218 | 218 | 1.09
F88-2 | 818 | SR-Z |  | 110 | 123 | 123 | 1.1182
F88-3 | 817 | SR-ZA |  | 60 | 71 | 71 | 1.1833
SA TOTAL |  |  |  | 370 | 412 | 412 | 1.1135
R88-1 | 819 | RR-9 | 8 | 200 | 412 | 412 | 2.06
RA TOTAL |  |  |  | 200 | 421 | 412 | 2.06
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU08-9
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
50 |  | Area: 804
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Unit only rated for 2200 CFM per submitals. Filters clogged; removed for testing. Amperage is for both motors at the same time. Bedroom diffusers brought as close to design without whisteling.
Model Num | HPPR022W4R411R000 |  |  |  | SA CFM | 2430 | 1921
Serial Num | 356318-2 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2430 | 1921
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 12.5
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.45"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.41"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.86"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.811
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F89-1 | BED | SR | 10 | 255 | 346 | 263 | 1.0314
F89-2 | BED | SR | 10 | 255 | 313 | 314 | 1.2314
F89-3 | LIVING | SR | 10 | 320 | 221 | 232 | 0.725
F89-4 | LIVING | SR | 10 | 320 | 162 | 221 | 0.69063
F89-5 | LIVING | SR | 10 | 320 | 204 | 215 | 0.67188
F89-6 | LIVING | SR | 10 | 320 | 220 | 224 | 0.7
F89-7 | LIVING | SR | 10 | 320 | 196 | 227 | 0.70937
F89-8 | LIVING | SR | 10 | 320 | 209 | 225 | 0.70312
SA TOTAL |  |  |  | 2430 | 1871 | 1921 | 0.79053
R89-1 |  | RR | 30X30 | 2430 | 1871 | 1921 | 0.79053
RA TOTAL |  |  |  | 2430 | 1871 | 1921 | 0.79053
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU09-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU09-1 (FCU-G1) |  | Area: 905
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes
Model Num | HPPR022W4R411R000 |  |  |  | SA CFM | 2580 | 2047 | Fan speed high
Serial Num | 356318-1 |  |  |  | Fan RPM |  | NA | Amps read are for both motors
[5 empty] | OA CFM | 0 | 0 | Unit only rated for 2200 CFM per submittals.
[5 empty] | RA CFM | 2580 | 2047
Motor Data |  |  |  |  | RL Voltage |  | 121.1
Motor MFG | NA |  |  |  | RL Amperage |  | 14.32
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.10"
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.18"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.28"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.49
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F91-1 | BED 1 | SR | 10 | 380 | 268 | 300 | 0.78947
F91-2 | BED 2 | SR | 10 | 300 | 294 | 249 | 0.83
F91-3 | BED 2 | SR | 10 | 300 | 308 | 227 | 0.75667
F91-4 | LIVING | SR | 10 | 320 | 198 | 255 | 0.79688
F91-5 | LIVING | SR | 10 | 320 | 246 | 243 | 0.75938
F91-6 | LIVING | SR | 10 | 320 | 272 | 268 | 0.8375
F91-7 | LIVING | SR | 10 | 320 | 287 | 242 | 0.75625
F91-8 | LIVING | SR | 10 | 320 | 174 | 263 | 0.82188
SA TOTAL |  |  |  | 2580 | 2047 | 2047 | 0.79341
R91-1 |  | RR | 28X28 | 2580 | 2047 | 2047
RA TOTAL |  |  |  | 2580 | 2047 | 2047 | 0.79341
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU09-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU09-2 (FCU-Q) |  | Area: 901
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR010W4R411R000 |  |  |  | SA CFM | 990 | 1002 | Notes
Serial Num | 356318-5 |  |  |  | FAN SPEED |  | MED | Fan speed medium
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 990 | 1002
Motor Data |  |  |  |  | RL Voltage |  | 123.3
Motor MFG | NA |  |  |  | RL Amperage |  | 3.9
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.8"
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.24"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.32"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.167
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F92-1 | STUDIO | SR | 10 | 330 | 450 | 329 | 0.99697
F91-2 | STUDIO | SR | 10 | 330 | 214 | 333 | 1.0091
F91-3 | STUDIO | SR | 10 | 330 | 489 | 340 | 1.0303
SA TOTAL |  |  |  | 990 |  | 1002 | 1.0121
R92-1 |  | RR | 18X18 | 990 |  | 1002 | 1.0121
RA TOTAL |  |  |  | 990 |  | 1002 | 1.0121
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU09-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU09-3 (FCU-B1) |  | Area: 902
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR015W4R411L000 |  |  |  | SA CFM | 1740 | 1419 | Notes
Serial Num | 356318-3 |  |  |  | FAN SPEED |  | HIGH | Amperage for both motors at the same time.
[5 empty] | OA CFM | 0 | NA | Balanced at high speed setpoint.
[5 empty] | RA CFM | 1740 | 1419 | Unit only capable of 1500 CFM per submitals.
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NA |  |  |  | RL Amperage |  | 6.1
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.11"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.15"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.26"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.201
Amperage (rated) | 5
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F93-1 | LIVING | SR | 10 | 305 | 250 | 246 | 0.80656
F93-2 | LIVING | SR | 10 | 310 | 316 | 243 | 0.78387
F93-3 | LIVING | SR | 10 | 305 | 225 | 249 | 0.81639
F93-4 | BED | SR | 10 | 275 | 341 | 227 | 0.82545
F93-5 | BED | SR | 10 | 270 | 456 | 225 | 0.83333
F93-6 | BED | SR | 10 | 275 | 477 | 226 | 0.82182
SA TOTAL |  |  |  | 1740 | 2065 | 1419 | 0.81552
R93-1 |  | RR | 22X22 | 1740 | 1419 | 1419 | 0.81
RA TOTAL |  |  |  | 1740 | 1419 | 1419 | 0.81
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU09-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU09-4 (FCU-D) |  | Area: 907
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R321R000 |  |  |  | SA CFM | 670 | 695 | Notes
Serial Num | 356318-6 |  |  |  | FAN SPEED |  | LOW | Incorrect speed wires ran from unit to thermostat, limited to 2 speed
[5 empty] | OA CFM | 0 | NA | Unit balanced at low speed setpoint
[5 empty] | RA CFM | 670 | 695
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NA |  |  |  | RL Amperage |  | 1.3
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.06"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.07"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.13"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.085
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F94-1 | LIVING | SR | 10 | 305 | 220 | 308 | 1.01
F94-2 | LIVING | SR | 10 | 305 | 283 | 325 | 1.07
F94-3 | LIVING | SR | 10 | 60 | 226 | 62 | 1.03
SA TOTAL |  |  |  | 670 | 729 | 695 | 1.04
R94-1 |  | RR | 16X16 | 670 |  | 695 | 1.04
RA TOTAL |  |  |  | 670 | 729 | 695 | 1.04
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU09-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU09-5 (FCU-E) |  | Area: 908
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Medium speed setpoint. Diffuser 2 fully closed, unable to reduce CFM.
Model Num | HPPR006W4R211R000 |  |  |  | SA CFM | 370 | 352
Serial Num | 356318-7 |  |  |  | FAN SPEED |  | MED
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 370 | 352
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 1.5
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.10"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.25"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.35"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.099
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F95-1 | LIVING | SR | 10 | 310 | 283 | 283 | 0.9129
F95-2 | LIVING | SR | 10 | 60 | 69 | 69 | 1.15
SA TOTAL |  |  |  | 370 | 352 | 352 | 0.95135
R95-1 |  | RR | 12X12 | 370 | 352 | 352 | 0.95135
RA TOTAL |  |  |  | 370 | 352 | 352 | 0.95135
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU09-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU09-6 (FCU-B2) |  | Area: 903
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR015W4R411R000 |  |  |  | SA CFM | 1740 | 1457
Serial Num | 356318-4 |  |  |  | FAN SPEED |  | HIGH
[5 empty] | OA CFM | 0 | 0 | NOTES
[5 empty] | RA CFM | 1740 | 1457 | HIGH FAN SPEED SETPOINT
Motor Data |  |  |  |  | RL Voltage |  | 122 | AMPERAGE IS FOR BOTH MOTORS AT THE SAME TIME
Motor MFG | NA |  |  |  | RL Amperage |  | 5.7 | SUBMITTALS INDICATE UNIT CAN ONLY REACH 1500 CFM
Horsepower | 0.33 |  |  |  | Suction ESP |  | 0.10" | Unit only capable of 1500 CFM per submitals
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.11"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.21"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.188
Amperage (rated) | 5
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F96-1 | BED | SR | 10 | 275 | 233 | 233 | 0.84727
F96-2 | BED | SR | 10 | 270 | 227 | 227 | 0.84074
F96-3 | BED | SR | 10 | 275 | 232 | 232 | 0.84364
F96-4 | LIVING | SR | 10 | 305 | 261 | 261 | 0.85574
F96-5 | LIVING | SR | 10 | 305 | 246 | 246 | 0.80656
F96-6 | LIVING | SR | 10 | 310 | 258 | 258 | 0.83226
SA TOTAL |  |  |  | 1740 | 1457 | 1457 | 0.83736
R96-1 |  | RR | 24X24 | 1740 | 1457 | 1457 | 1.06
RA TOTAL |  |  |  | 1740 | 1457 | 1841 | 1.06
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU09-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU09-7 (FCU-F) |  | Area: 910
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R421R000 |  |  |  | SA CFM | 780 | 787
Serial Num | 356318-8 |  |  |  | FAN SPEED |  | HIGH
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 780 | 787
Motor Data |  |  |  |  | RL Voltage |  | 120
Motor MFG | NL |  |  |  | RL Amperage |  | 4.62
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.10"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.16"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.26"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.304
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F97-1 | BED | SR | 10 | 230 | 243 | 243 | 1.0565
F97-2 | LIVING | SR | 10 | 180 | 182 | 182 | 1.0111
F97-3 | LIVING | SR | 10 | 185 | 171 | 171 | 0.92432
F97-4 | LIVING | SR | 10 | 185 | 191 | 191 | 1.0324
SA TOTAL |  |  |  | 780 | 787 | 787 | 1.009
R97-1 |  | RR | 16X16 | 780 | 787 | 787 | 1.009
RA TOTAL |  |  |  | 780 | 787 | 787 | 1.009
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU09-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU09-8 (FCU-LOBBY) |  | Area: 919
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211 |  |  |  | SA CFM | 370 | 392
Serial Num | 356318-9 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 200 | 392
Motor Data |  |  |  |  | RL Voltage |  | 122.6
Motor MFG | NL |  |  |  | RL Amperage |  | 3.25
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.70"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.36"
Phase | 1 |  |  |  | Total ESP | 0.4 | 1.06"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.21"
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | . Filter removed for testing
F98-1 | 919 | CD-1 |  | 200 | 312 | 211 | 1.055 | . Medium fan speed
F98-2 | 918 | SR-Z |  | 110 | 82 | 118 | 1.0727 | . Supply air and return air numbers are not compatible with 0 outside air, return damper left full open
F98-3 | 917 | SR-ZA |  | 60 | 78 | 63 | 1.05
SA TOTAL |  |  |  | 370 |  | 392 | 1.0595
R98-1 | 919 | RR-9 | 8 | 200 |  |  | 0
RA TOTAL |  |  |  | 200 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU09-9
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU09-9 (FCU-A2) |  | Area: 904
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022W4R411R |  |  |  | SA CFM | 2430 | 2127
Serial Num | 356318-2 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2430 | 2127
Motor Data |  |  |  |  | RL Voltage |  | 117.2
Motor MFG | NL |  |  |  | RL Amperage |  | 12.36
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.37"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.34"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.71"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.4
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | . Filters removed for testing, unit below design.
F99-1 | BED | SR | 10 | 255 | 365 | 245 | 0.96078 | . High fan speed
F99-2 | BED | SR | 10 | 255 | 297 | 248 | 0.97255 | . Unit equipped with 2 fan motors
F99-3 | LIVING | SR | 10 | 320 | 271 | 295 | 0.92188
F99-4 | LIVING | SR | 10 | 320 | 210 | 225 | 0.70312
F99-5 | LIVING | SR | 10 | 320 | 225 | 229 | 0.71562
F99-6 | LIVING | SR | 10 | 320 | 190 | 220 | 0.6875
F99-7 | LIVING | SR | 10 | 320 | 298 | 322 | 1.0063
F99-8 | LIVING | SR | 10 | 320 | 315 | 343 | 1.0719
SA TOTAL |  |  |  | 2430 |  | 2127 | 0.87531
R99-1 |  | RR | 30X30 | 2430 |  |  | 0
RA TOTAL |  |  |  | 2430 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU10-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU10-1 (FCU-G1) |  | Area: 1005
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022W4R411R000 |  |  |  | SA CFM | 2580 | 1971 | Notes: Cannot enter max high speed; high speed tap does not recive 28VAC. Putting medium speed wire on high speed tap only allows the unit to do 1971 CFM. Prelim CFM on Medium speed. Unit filters clean. Unit balance proportionally. Amperage is for both motors at the same time. Per submitals unit is only rated for 2200 CFM.
Serial Num | 356318-1 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2580 | 1971
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 12.4
Horsepower | 0.50 |  |  |  | Suction ESP |  | -0.10"
Motor Rpm | NL |  |  |  | Discharge ESP |  | .017"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.27"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.4
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F101-1 | BED 1 | SR | 10 | 380 | 188 | 308 | 0.81053
F101-2 | BED 2 | SR | 10 | 300 | 193 | 213 | 0.71
F101-3 | BED 2 | SR | 10 | 300 | 174 | 235 | 0.78333
F101-4 | LIVING | SR | 10 | 320 | 173 | 224 | 0.7
F101-5 | LIVING | SR | 10 | 320 | 198 | 244 | 0.7625
F101-6 | LIVING | SR | 10 | 320 | 170 | 234 | 0.73125
F101-7 | LIVING | SR | 10 | 320 | 218 | 254 | 0.79375
F101-8 | LIVING | SR | 10 | 320 | 198 | 259 | 0.80937
SA TOTAL |  |  |  | 2580 | 1512 | 1971 | 0.76395
R101-1 |  | RR | 28X28 | 2580
RA TOTAL |  |  |  | 2580 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU10-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU10-2 (FCU-Q) |  | Area: 1001
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR010W4R411R000 |  |  |  | SA CFM | 990 | 1062 | Notes: High speed setpoint.
Serial Num | 356318-5 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 990 | 1062
Motor Data |  |  |  |  | RL Voltage |  | 119
Motor MFG | NL |  |  |  | RL Amperage |  | 7.1
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.09"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.21"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.30"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.461
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F102-1 | STUDIO | SR | 10 | 330 | 348 | 348 | 1.0545
F102-2 | STUDIO | SR | 10 | 330 | 353 | 353 | 1.0697
F102-3 | STUDIO | SR | 10 | 330 | 361 | 361 | 1.0939
SA TOTAL |  |  |  | 990 | 1062 | 1062 | 1.0727
R102-1 |  | RR | 18X18 | 990 | 1062 | 1062 | 1.0727
RA TOTAL |  |  |  | 990 | 1062 | 1062 | 1.0727
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU10-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU10-3 (FCU-B1) |  | Area: 1002
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Submittals indicate unit only capable of 1500 CFM. Confirmed at max fan speed. Confirmed unit filters clean. Unit balanced proportionally.
Model Num | HPPR015W4R411L000 |  |  |  | SA CFM | 1740 | 1316
Serial Num | 356318-3 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1374
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 4.78
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.06"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.12"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.018"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.31
Amperage (rated) | 5
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F103-1 | LIVING | SR | 10 | 305 | 231 | 231 | 0.75738
F103-2 | LIVING | SR | 10 | 310 | 226 | 226 | 0.72903
F103-3 | LIVING | SR | 10 | 305 | 240 | 240 | 0.78689
F103-4 | BED | SR | 10 | 275 | 211 | 211 | 0.76727
F103-5 | BED | SR | 10 | 270 | 194 | 194 | 0.71852
F103-6 | BED | SR | 10 | 275 | 214 | 214 | 0.77818
SA TOTAL |  |  |  | 1740 | 1316 | 1316 | 0.75632
R103-1 |  | RR | 22X22 | 1740 | 1316 | 1316 | 0.75632
RA TOTAL |  |  |  | 1740 | 1316 | 1316 | 0.75632
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU10-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU10-4 (FCU-D) |  | Area: 1007
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | NOTE: High fan speed setpoint. Diffuser 3 set to lowest setpoint without whistleing.
Model Num | HPPR008W4R321R000 |  |  |  | SA CFM | 670 | 717
Serial Num | 356318-6 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 670 | 717
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 4.35
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.23"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.26"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.49"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.287
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F104-1 | LIVING | SR | 10 | 305 | 253 | 275 | 0.90164
F104-2 | LIVING | SR | 10 | 305 | 294 | 281 | 0.92131
F104-3 | LIVING | SR | 10 | 60 | 183 | 161 | 2.6833
SA TOTAL |  |  |  | 670 | 730 | 717 | 1.0701
R104-1 |  | RR | 16X16 | 670 | 730 | 717 | 1.0701
RA TOTAL |  |  |  | 670 | 730 | 717 | 1.0701
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU10-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU10-5 (FCU-E) |  | Area: 1008
Unit Data |  |  |  |  | Test Data |  |  | NOTES: Unable to reduce diffuser 2 CFM; Damper Fully closed. Medium speed setpoint.
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211R000 |  |  |  | SA CFM | 370 | 366
Serial Num | 356318-7 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 370 | 366
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 1.5
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.15"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.16"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.31"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.09
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F105-1 | LIVING | SR | 10 | 310 | 287 | 287 | 0.93
F105-2 | LIVING | SR | 10 | 60 | 79 | 79 | 1.32
SA TOTAL |  |  |  | 370 | 366 | 366 | 0.99
R105-1 |  | RR | 12X12 | 370 | 366 | 366 | 0.99
RA TOTAL |  |  |  | 370 | 366 | 366 | 0.99
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU10-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU10-6 (FCU-B2) |  | Area: 1003
Unit Data |  |  |  |  | Test Data |  |  | NOTES: Unit confirmed in high fan speed. Filters confirmed clean. Based on submittals unit is only capable of 1500 CFM. Amperage is for both motors at the same time.
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR015W4R411R000 |  |  |  | SA CFM | 1740 | 1323
Serial Num | 356318-4 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1740 | 1355
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 5.42
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.09"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.12"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.21"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.178
Amperage (rated) | 5
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F106-1 | BED | SR | 10 | 275 | 201 | 201 | 0.73091
F106-2 | BED | SR | 10 | 270 | 199 | 205 | 0.75926
F106-3 | BED | SR | 10 | 275 | 201 | 217 | 0.78909
F106-4 | LIVING | SR | 10 | 305 | 268 | 221 | 0.72459
F106-5 | LIVING | SR | 10 | 305 | 210 | 242 | 0.79344
F106-6 | LIVING | SR | 10 | 310 | 244 | 237 | 0.76452
SA TOTAL |  |  |  | 1740 | 1323 | 1323 | 0.76034
R106-1 |  | RR | 24X24 | 1740 | 1355 | 1355 | 1355
RA TOTAL |  |  |  | 1740 | 1355 | 1355 | 1355
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU10-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU10-7 (FCU-F) |  | Area: 1010
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R421R000 |  |  |  | SA CFM | 780 | 767
Serial Num | 356318-8 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 780 | 767
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 3.9
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.12"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.15
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.27"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.257
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F107-1 | BED | SR | 10 | 230 | 206 | 206 | 0.89565
F107-2 | LIVING | SR | 10 | 180 | 196 | 196 | 1.0889
F107-3 | LIVING | SR | 10 | 185 | 187 | 187 | 1.0108
F107-4 | LIVING | SR | 10 | 185 | 178 | 178 | 0.96216
SA TOTAL |  |  |  | 780 | 767 | 767 | 0.98333
R107-1 |  | RR | 16X16 | 780 | 767 | 767 | 0.98333
RA TOTAL |  |  |  | 780 | 767 | 767 | 0.98333
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU10-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU10-8 (FCU-LOBBY) |  | Area: 1019
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R211L000 |  |  |  | SA CFM | 370 | 428 | Notes: It is not possible to have only 200 return air with 0 oa and have a unit total of 370 CFM. Return air is set fully open to allow the unit to have correct supply total. Filters clogged, Removed for testing. Speed set to medium as low was 270 CFM. Total CFM should be closer to design when a clean filter is installed.
Serial Num | 356318-9 |  |  |  | Fan Speed |  | Medium
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 200 | 428
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 1.57
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.44"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.14"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.58"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.951
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F108-1 | 919 | CD-1 |  | 200 | 241 | 241 | 1.205
F108-2 | 918 | SR-Z |  | 110 | 112 | 112 | 1.0182
F108-3 | 917 | SR-ZA |  | 60 | 75 | 75 | 1.25
SA TOTAL |  |  |  | 370 | 428 | 428 | 1.1568
R108-1 | 919 | RR-9 | 8 | 200 | 428 | 428 | 2.14
RA TOTAL |  |  |  | 200 | 428 | 428 | 2.14
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU10-9
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU10-9 (FCU-A2) |  | Area: 1004
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022W4R411R000 |  |  |  | SA CFM | 2430 | 2079 | Notes: Unit only rated for 2200 CFM per submittals. Filters clogged and were removed for testing. Amps are for both motors at the same time. Bedroom balanced to design all others balanced proportionally.
Serial Num | 356318-2 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2430 | 2079
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 13
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.21"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.31"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.52"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.844
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F109-1 | BED | SR | 10 | 255 | 278 | 245 | 0.96078
F109-2 | BED | SR | 10 | 255 | 333 | 259 | 1.0157
F109-3 | LIVING | SR | 10 | 320 | 184 | 269 | 0.84062
F109-4 | LIVING | SR | 10 | 320 | 215 | 253 | 0.79063
F109-5 | LIVING | SR | 10 | 320 | 221 | 267 | 0.83437
F109-6 | LIVING | SR | 10 | 320 | 195 | 257 | 0.80312
F109-7 | LIVING | SR | 10 | 320 | 238 | 258 | 0.80625
F109-8 | LIVING | SR | 10 | 320 | 271 | 271 | 0.84688
SA TOTAL |  |  |  | 2430 | 1935 | 2079 | 0.85556
R109-1 |  | RR | 30X30 | 2430 | 1935 | 2079 | 0.85556
RA TOTAL |  |  |  | 2430 | 1935 | 2079 | 0.85556
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU11-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU11-1 (FCU-G) |  | Area: 1101
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022W4R411R000 |  |  |  | SA CFM | 1650 | 1736 | NOTES:
Serial Num | 356687-2 |  |  |  | Fan Speed |  | HIGH | Amperage is for both motors at the same time.
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1650 | 1736
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 12.1
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.59"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.49"
Phase | 1 |  |  |  | Total ESP | 0.4 | 1.08"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.785
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F111-1 | BED 2 | SR | 10 | 330 | 349 | 349 | 1.0576
F111-2 | BED 1 | SR | 10 | 330 | 358 | 358 | 1.0848
F111-3 | LIVING | SR | 10 | 330 | 352 | 352 | 1.0667
F111-4 | LIVING | SR | 10 | 330 | 332 | 332 | 1.0061
F111-5 | LIVING | SR | 10 | 330 | 345 | 345 | 1.0455
SA TOTAL |  |  |  | 1650 | 1736 | 1736 | 1.0521
R111-1 |  | RR | 22X22 | 1650 | 1736 | 1736 | 1.0521
RA TOTAL |  |  |  | 1650 | 1736 | 1736 | 1.0521
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU11-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU11-2 (FCU-H) |  | Area: 1102
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR010 |  |  |  | SA CFM | 940 | 917
Serial Num | 356687-3 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 940 | 921
Motor Data |  |  |  |  | RL Voltage |  | 124.7
Motor MFG | NL |  |  |  | RL Amperage |  | 7.2
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.47"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.27"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.74"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Fan speed set pt. high
F112-1 |  |  |  | 50 | 68 | 72 | 1.44 | Diffuser 1 above design with faced amper fully closed
F112-2 |  |  |  | 290 | 255 | 270 | 0.93103
F112-3 |  |  |  | 300 | 230 | 302 | 1.0067
F112-4 |  |  |  | 300 | 214 | 273 | 0.91
SA TOTAL |  |  |  | 940 |  | 917 | 0.97553
R112-1 |  |  |  | 940 | 787 | 921 | 0.97979
RA TOTAL |  |  |  | 940 |  | 921 | 0.97979
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU11-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU11-3 (FCU-I) |  | Area: 1103
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR010 |  |  |  | SA CFM | 920 | 926
Serial Num | 356687-4 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 920 | 921
Motor Data |  |  |  |  | RL Voltage |  | 125.4
Motor MFG | NL |  |  |  | RL Amperage |  | 5.8
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.43"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.20"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.63"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Dirty filters, removed for testing
F113-1 | BED | SR | 6 | 50 | 136 | 102 | 2.04 | Fan speed medium
F113-2 | LIVING | SR | 10 | 290 | 260 | 295 | 1.0172 | Diffuser 1 above design, face damper fully closed
F113-3 | LIVING | SR | 10 | 290 | 187 | 262 | 0.90345
F113-4 | LIVING | SR | 10 | 290 | 258 | 267 | 0.92069
SA TOTAL |  |  |  | 920 |  | 926 | 1.0065
R113-1 |  | RR | 16X16 | 920 | 921 | 921 | 1.0011
RA TOTAL |  |  |  | 920 |  | 921 | 1.0011
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU11-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU11-4 (FCU-J) |  | Area: 1104
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR010W4R411R000 |  |  |  | SA CFM | 930 | 1011
Serial Num | 356687-6 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 930 | 1011
Motor Data |  |  |  |  | RL Voltage |  | 123
Motor MFG | NL |  |  |  | RL Amperage |  | 6.3
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.23"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.29"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.52"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.409
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F114-1 | BED | SR | 6 | 50 | 53 | 53 | 1.06
F114-2 | LIVING | SR | 10 | 290 | 315 | 315 | 1.0862
F114-3 | LIVING | SR | 10 | 295 | 324 | 324 | 1.0983
F114-4 | LIVING | SR | 10 | 295 | 319 | 319 | 1.0814
SA TOTAL |  |  |  | 930 | 1011 | 1011 | 1.0871
R114-1 |  | RR | 16X16 | 930 | 1011 | 1011 | 1.0871
RA TOTAL |  |  |  | 930 | 1011 | 1011 | 1.0871
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU11-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU11-5 (FCU-CORRIDOR) |  | Area: 1109 CORRIDOR
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR008W4R321R |  |  |  | SA CFM | 700 | 608 | Notes: Fan Speed High. Return flexed instead of hard-piped like others. Unit below design.
Serial Num | 3568687-1 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 700 | 592
Motor Data |  |  |  |  | RL Voltage |  | 124.2
Motor MFG | NL |  |  |  | RL Amperage |  | 5.06
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.85"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.16"
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F115-1 | 1109 | SR | 8 | 175 | 154 | 154 | 0.88
F115-2 | 1109 | SR | 8 | 175 | 171 | 171 | 0.97714
F115-3 | 1109 | SR | 8 | 175 | 145 | 145 | 0.82857
F115-4 | 1109 | SR | 8 | 175 | 138 | 138 | 0.78857
SA TOTAL |  |  |  | 700 |  | 608 | 0.86857
R115-1 | 1109 | RR | 12X12 | 700 | 592 | 592 | 0.84571
RA TOTAL |  |  |  | 700 |  | 592 | 0.84571
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU11-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU11-6 (FCU-J) |  | Area: 1105
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Unit filters clogged, removed for testing. Unable to reduce supply grill 1 any further, damper fully closed.
Model Num | HPPR010W4R411L000 |  |  |  | SA CFM | 930 | 981
Serial Num | 356687-5 |  |  |  | Fan Setpoint |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 930 | 1047
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | N; |  |  |  | RL Amperage |  | 6.4
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.31"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.47"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.78"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.41558
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F116-1 | BED | SR | 8 | 50 | 118 | 85 | 1.7
F116-2 | LIVING | SR | 10 | 290 | 308 | 316 | 1.0897
F116-3 | LIVING | SR | 10 | 295 | 279 | 291 | 0.98644
F116-4 | LIVING | SR | 10 | 295 | 294 | 289 | 0.97966
SA TOTAL |  |  |  | 930 | 999 | 981 | 1.0548
R116-1 |  | RR | 16X16 | 930 | 1055 | 1047 | 1.1258
RA TOTAL |  |  |  | 930 | 1055 | 1047 | 1.1258
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU11-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU11-7 (FCU-J) |  | Area: 1106
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Filter Clogged, removed for testing. Prelim reading with filter in. Unable to reduce supply grill 1 any further, damper fully closed. Medium speed setpoint 80% of design set fan speed to high speed.
Model Num | HPPR010W4R411L000 |  |  |  | SA CFM | 930 | 1006
Serial Num | 356687-5 |  |  |  | Fan Setpoint |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 930 | 1006
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 7.1
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.31"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.34"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.65"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.46104
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F117-1 | BED | SR | 8 | 50 | 66 | 108 | 2.16
F117-2 | LIVING | SR | 10 | 290 | 129 | 281 | 0.96897
F117-3 | LIVING | SR | 10 | 295 | 156 | 311 | 1.0542
F117-4 | LIVING | SR | 10 | 295 | 144 | 306 | 1.0373
SA TOTAL |  |  |  | 930 | 495 | 1006 | 1.0817
R117-1 |  | RR | 16X16 | 930 | 525 | 1071 | 1.1516
RA TOTAL |  |  |  | 930 | 525 | 1071 | 1.1516
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU11-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU11-8 (FCU-LOBBY) |  | Area: ELEV LOBBY
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR006W4R421L |  |  |  | SA CFM | 390 | 417
Serial Num | 356687-9 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM |  | 0
[5 empty] | RA CFM | 350 | 411
Motor Data |  |  |  |  | RL Voltage |  | 122.2
Motor MFG | NL |  |  |  | RL Amperage |  | 3.18
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.77"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.13"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.9"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.21
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F118-1 | 1116 | SR | 8 | 40 | 65 | 43 | 1.075
F118-2 | 1117 | SR | 8 | 150 | 138 | 156 | 1.04
F118-3 | LOBBY | CD | 8 | 200 | 243 | 218 | 1.09
SA TOTAL |  |  |  | 390 |  | 417 | 1.0692
R118-1 | LOBBY | RR | 8 | 200 | 245 | 245 | 1.225
R118-2 | 1117 | RR | 8 | 150 | 162 | 172 | 1.1467
RA TOTAL |  |  |  | 350 |  | 417 | 1.1914
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU11-9
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU11-9 (FCU-K) |  | Area: 1107
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num |  |  |  |  | SA CFM | 1000 |  | Notes: Room, not finished 12/23/2024 12/27 .Unit missing thermostat
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 0
[5 empty] | RA CFM | 1000
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP | 0.4
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F119-1 | BED | SR | 8 | 100 |  |  | 0
F119-2 | LIVING | SR | 10 | 300 |  |  | 0
F119-3 | LIVING | SR | 10 | 300 |  |  | 0
F119-4 | LIVING | SR | 10 | 300 |  |  | 0
SA TOTAL |  |  |  | 1000 |  | 0 | 0
R119-1 |  | RR | 16X16 | 1000 |  |  | 0
RA TOTAL |  |  |  | 1000 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU11-10
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU11-10 (FCU-L) |  | Area: 1108
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Unit in high speed. Amperage reflects both motors
Model Num | HPPE022W4R411R000 |  |  |  | SA CFM | 2200 | 2012
Serial Num | 356687-8 |  |  |  | Fan RPM |  | NA
[5 empty] | OA CFM |  | 0
[5 empty] | RA CFM |  | 1769
Motor Data |  |  |  |  | RL Voltage |  | 122.4
Motor MFG | NL |  |  |  | RL Amperage |  | 13.21
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.66"
Motor Rpm | N |  |  |  | Discharge ESP |  | 0.26"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.92"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.42
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1110-1 | 1108 BED | SR | 12X8 | 180 | 183 | 164 | 0.91111
1110-2 | 1108 BED | SR | 12X8 | 180 | 212 | 192 | 1.0667
1110-3 | 1108 STUDY | SR | 12X8 | 40 | 128 | 36 | 0.9
1110-4 | 1108 LIVING | SR | 12X8 | 360 | 278 | 328 | 0.91111
1110-5 | 1108 LIVING | SR | 12X8 | 360 | 310 | 332 | 0.92222
1110-6 |  |  |  | 360 | 322 | 317 | 0.88056
1110-7 |  |  |  | 360 | 292 | 311 | 0.86389
1110-8 |  |  |  | 360 | 302 | 332 | 0.92222
SA TOTAL |  |  |  | 2200 |  | 2012 | 0.91455
RA TOTAL |  |  |  | 2200 |  |  | 0
|  |  |  | 2200 | 1769 | 1769 | 0.80409
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU12-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU12-1 (FCU-G) |  | Area: 1201 (1210)
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Low speed setpoint too low (66% of design) Fan speed set to Medium and balanced proportionally. Unit changed to 2 speed (Medium and Low)
Model Num | HPPR022W4R411R |  |  |  | SA CFM | 1650 | 1848
Serial Num | 356687-2 |  |  |  | Fan Speed |  | Medium
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 1650 | 1848
Motor Data |  |  |  |  | RL Voltage |  | 122
Motor MFG | NL |  |  |  | RL Amperage |  | 10.7
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.16"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.33"
Phase | 1 |  |  |  | Total ESP |  | 0.49"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.694
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F121-1 | BED 2 | SR | 10 | 330 | 367 | 366 | 1.1091
F121-2 | BED 1 | SR | 10 | 330 | 433 | 372 | 1.1273
F121-3 | LIVING | SR | 10 | 330 | 395 | 363 | 1.1
F121-4 | LIVING | SR | 10 | 330 | 344 | 369 | 1.1182
F121-5 | LIVING | SR | 10 | 330 | 292 | 378 | 1.1455
SA TOTAL |  |  |  | 1650 | 1831 | 1848 | 1.12
R121-1 |  | RR | 22X22 | 1650 | 1831 | 1848 | 1.12
RA TOTAL |  |  |  | 1650 | 1831 | 1848 | 1.12
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU12-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU12-2 (FCU-H) |  | Area: 1202 (1211)
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Supply grill 3 reduced as much as possible without whistling.
Model Num | HPPR010W4R411L |  |  |  | SA CFM | 940 | 998
Serial Num | 356687-3 |  |  |  | Fan Speed |  | HIGH
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 940 | 998
Motor Data |  |  |  |  | RL Voltage |  | 122.8
Motor MFG | NL |  |  |  | RL Amperage |  | 6.55
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.52"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.23"
Phase | 1 |  |  |  | Total ESP |  | 0.75"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F122-1 | BED | SR | 6 | 50 | 108 | 82 | 1.64
F122-2 | LIVING | SR | 10 | 290 | 356 | 318 | 1.0966
F122-3 | LIVING | SR | 10 | 300 | 322 | 298 | 0.99333
F122-4 | LIVING | SR | 10 | 300 | 203 | 300 | 1
SA TOTAL |  |  |  | 940 | 989 | 998 | 1.0617
R122-1 |  | RR | 16X16 | 940 | 989 | 998 | 1.0617
RA TOTAL |  |  |  | 940 | 989 | 998 | 1.0617
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU12-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU12-3 (FCU-I) |  | Area: 1203 (1212)
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Supply grill 1 unable to reduce any further without whistling.
Model Num | HPPR010W4R4 |  |  |  | SA CFM | 920 | 982
Serial Num | 356687-4 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 920 | 982
Motor Data |  |  |  |  | RL Voltage |  | 120 | FINALS: GM
Motor MFG | NL |  |  |  | RL Amperage |  | 6.3
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.53
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.28
Phase | 1 |  |  |  | Total ESP |  | 0.81
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.41
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F123-1 | BED | SR | 6 | 50 | 153 | 128 | 2.56
F123-2 | LIVING | SR | 10 | 290 | 258 | 265 | 0.91379
F123-3 | LIVING | SR | 10 | 290 | 288 | 294 | 1.0138
F123-4 | LIVING | SR | 10 | 290 | 310 | 295 | 1.0172
SA TOTAL |  |  |  | 920 | 1009 | 982 | 1.0674
R123-1 |  | RR | 16X16 | 920 | 1009 | 982 | 1.0674
RA TOTAL |  |  |  | 920 | 1009 | 982 | 1.0674
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU12-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU12-4 (FCU-J) |  | Area: 1204(1213)
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Note: Supply grill 1 lowered as much as possible without whistling.
Model Num | HPPR010W4R4 |  |  |  | SA CFM | 930 | 968
Serial Num | 356687-6 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 930 | 968
Motor Data |  |  |  |  | RL Voltage |  | 120
Motor MFG | NA |  |  |  | RL Amperage |  | 6.3 | FINALS:GM
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.69
Motor Rpm | NA |  |  |  | Discharge ESP |  | 0.21
Phase | 1 |  |  |  | Total ESP |  | 0.9
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.41
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F124-1 | BED | SR | 6 | 50 | 114 | 125 | 2.5
F124-2 | LIVING | SR | 10 | 290 | 277 | 272 | 0.93793
F124-3 | LIVING | SR | 10 | 295 | 261 | 290 | 0.98305
F124-4 | LIVING | SR | 10 | 295 | 346 | 281 | 0.95254
SA TOTAL |  |  |  | 930 | 998 | 968 | 1.0409
R124-1 |  | RR | 16X16 | 930 | 998 | 968 | 1.0409
RA TOTAL |  |  |  | 930 | 998 | 968 | 1.0409
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU12-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU12-5 (FCU-CORRIDOR) |  | Area: CORRIDOR 1209
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Could not get a good reading for discharge pressure due to ductwork configuration.
Model Num | HPPR008W4R321R000 |  |  |  | SA CFM | 700 | 713
Serial Num | 356687-1 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 700 | 713
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 3.9
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.20"
Motor Rpm | NL |  |  |  | Discharge ESP |  | NA
Phase | 1 |  |  |  | Total ESP |  | 0.20"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.257
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F125-1 |  |  |  | 175 | 170 | 170 | 0.97143
F125-2 |  |  |  | 175 | 185 | 185 | 1.0571
F125-3 |  |  |  | 175 | 183 | 183 | 1.0457
F125-4 |  |  |  | 175 | 175 | 175 | 1
SA TOTAL |  |  |  | 700 | 713 | 713 | 1.0186
R124-1 |  |  |  | 700 | 713 | 713 | 1.0186
RA TOTAL |  |  |  | 700 | 713 | 713 | 1.0186
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU12-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU12-6 (FCU-J-LH) |  | Area: 1205(1214)
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Supply grill 1 reduced as low as possible without whistling.
Model Num | HPPR010W4R411L |  |  |  | SA CFM | 930 | 943
Serial Num | 356687-5 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 930 | 943
Motor Data |  |  |  |  | RL Voltage |  | 122.4
Motor MFG | NL |  |  |  | RL Amperage |  | 6.48
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.65"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.19"
Phase | 1 |  |  |  | Total ESP |  | 0.84"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F126-1 | BED | SR | 8 | 50 | 131 | 138 | 2.76
F126-2 | LIVING | SR | 10 | 290 | 179 | 264 | 0.91034
F126-3 | LIVING | SR | 10 | 295 | 191 | 274 | 0.92881
F126-4 | LIVING | SR | 10 | 295 | 185 | 267 | 0.90508
SA TOTAL |  |  |  | 930 | 686 | 943 | 1.014
R126-1 |  | RR | 16X16 | 930 | 686 | 943 | 1.014
RA TOTAL |  |  |  | 930 | 686 | 943 | 1.014
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU12-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU12-7 (FCU-J) |  | Area: 1206
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR010W4R411L000 |  |  |  | SA CFM | 930 | 845 | Notes: Bedroom diffuser lowered as much as possible without whisteling.
Serial Num | 356387-5 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 930 | 845
Motor Data |  |  |  |  | RL Voltage |  | 123
Motor MFG | NL |  |  |  | RL Amperage |  | 3.4
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.11"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.07"
Phase | 1 |  |  |  | Total ESP |  | 0.18"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.883
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F127-1 | BED | SR | 8 | 50 | 103 | 103 | 2.06
F127-2 | LIVING | SR | 10 | 290 | 247 | 247 | 0.85172
F127-3 | LIVING | SR | 10 | 295 | 243 | 243 | 0.82373
F127-4 | LIVING | SR | 10 | 295 | 252 | 252 | 0.85424
SA TOTAL |  |  |  | 930 | 845 | 845 | 0.9086
R127-1 |  | RR | 16X16 | 930 | 845 | 845 | 0.9086
RA TOTAL |  |  |  | 930 | 845 | 845 | 0.9086
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU12-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU12-8 (FCU-LOBBY) |  | Area: ELEV LOBBY
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | Notes: Return and supply must match in absence of OA; Return set to same as supply. Supply grill 1 fully closed. Unit set to 2 speed (low and medium) Unit is not ducted with 2 return ducts.
Model Num | HPPR006W4R421L000 |  |  |  | SA CFM | 390 | 423
Serial Num | 356687-9 |  |  |  | Fan Speed |  | Medium
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 390 | 423
Motor Data |  |  |  |  | RL Voltage |  | 121
Motor MFG | NL |  |  |  | RL Amperage |  | 3.1
Horsepower | 0.33 |  |  |  | Suction ESP |  | -0.48"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.39"
Phase | 1 |  |  |  | Total ESP |  | 0.87"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.204
Amperage (rated) | 5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F118-1 | 1116 | SR | 8 | 40 | 46 | 46 | 1.15
F118-2 | 1117 | SR | 8 | 150 | 158 | 158 | 1.0533
F118-3 | LOBBY | CD | 8 | 200 | 219 | 219 | 1.095
SA TOTAL |  |  |  | 390 | 423 | 423 | 1.0846
R118-1 | LOBBY | RR | 8 | 200 | 423 | 423 | 2.115
R118-2 | 1117 | RR | 8 | 150 | 0 | 0 | 0
RA TOTAL |  |  |  | 350 | 423 | 423 | 1.2086
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU12-9
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU12-9 (FCU-K) |  | Area: 1207
Unit Data |  |  |  |  | Test Data |  |  | Notes: drywall not complete/ no grills installed.
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num |  |  |  |  | SA CFM
Serial Num |  |  |  |  | Fan RPM
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU12-10
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU12-10 (FCU-L) |  | Area: 1208
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual
Model Num | HPPR022W4R411R000 |  |  |  | SA CFM | 2200 | 2091 | Notes: Study grill lowered as much as possible without whisteling.
Serial Num | 356687-8 |  |  |  | Fan Speed |  | High
[5 empty] | OA CFM | 0 | 0
[5 empty] | RA CFM | 2200 | 2091
Motor Data |  |  |  |  | RL Voltage |  | NA
Motor MFG | NL |  |  |  | RL Amperage |  | NA
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.14"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.23"
Phase | 1 |  |  |  | Total ESP |  | 0.37"
Voltage (rated) | 120 |  |  |  | Brake HP |  | NA
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1210-1 | 1208 BED | SR | 12X8 | 180 | 250 | 163 | 0.90556
1210-2 | 1208 BED | SR | 12X8 | 180 | 201 | 173 | 0.96111
1210-3 | 1208 STUDY | SR | 12X8 | 40 | 131 | 63 | 1.575
1210-4 | 1208LIVING | SR | 12X8 | 360 | 262 | 343 | 0.95278
1210-5 | 1208 LIVING | SR | 12X8 | 360 | 273 | 368 | 1.0222
1210-6 |  |  |  | 360 | 334 | 330 | 0.91667
1210-7 |  |  |  | 360 | 303 | 323 | 0.89722
1210-8 |  |  |  | 360 | 300 | 328 | 0.91111
SA TOTAL |  |  |  | 2200 | 2054 | 2091 | 0.95045
RA TOTAL |  |  |  | 2200 | 2054 | 2091 | 0.95045
|  |  |  | 2200 | 2054 | 2091 | 0.95045
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU13-1
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU13-1 (FCU-M-2) |  | Area: 1301
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | COOL | HEAT
Model Num | HPPR010W4R411R000 |  |  |  | SA CFM | 1730 | 1281 | 4.2 GPM | 2.1 GPM
Serial Num | 356687-11 |  |  |  | Fan Speed |  | HIGH
[5 empty] | OA CFM |  | 0
[5 empty] | RA CFM |  | 1281 | Unit undersized; unit only rated for 1000 CFM. Filter clogged and was removed for testing.
Motor Data |  |  |  |  | RL Voltage | 120 | 124
Motor MFG | NL |  |  |  | RL Amperage |  | 4
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.04"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.04"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.08"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.27
Amperage (rated) | 7.7
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F131-1 | LIVING | LD-1 | 8 | 175 | 123 | 123 | 0.70286
F131-2 | KITCHEN | LD-1 | 8 | 175 | 131 | 131 | 0.74857
F131-3 | KITCHEN | LD-1 | 8 | 175 | 128 | 128 | 0.73143
F131-4 | LIVING | LD-1 | 8 | 170 | 129 | 129 | 0.75882
F131-5 | LIVING | LD-1 | 8 | 170 | 122 | 122 | 0.71765
F131-6 | LIVING | LD-1 | 8 | 175 | 125 | 125 | 0.71429
F131-7 | LIVING | LD-1 | 8 | 175 | 132 | 132 | 0.75429
F131-8 | LIVING | LD-1 | 8 | 170 | 127 | 127 | 0.74706
F131-9 | LIVING | LD-1 | 8 | 170 | 133 | 133 | 0.78235
F131-10 | LIVING | LD-1 | 8 | 175 | 131 | 131 | 0.74857
FCU13-1 |  |  |  | 1730 | 1281 | 1281 | 0.74046
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU13-2
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU13-2 (FCU-M-1) |  | Area: 1301
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | COOL | HEAT
Model Num | HPPR010W4R411R000 |  |  |  | SA CFM | 1230 |  | 4.2 GPM | 2.1 GPM
Serial Num |  |  |  |  | Fan Speed
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 120
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F132-1 | BED 3 | LD-1 | 10 | 215 |  |  | 0
F132-2 | BED 3 | LD-1 | 10 | 215 |  |  | 0
F132-3 | BED 1 | LD-1 | 10 | 190 |  |  | 0
F132-4 | BED 1 | LD-1 | 10 | 190 |  |  | 0
F132-5 | BED 2 | LD-1 | 10 | 210 |  |  | 0
F132-6 | BED 2 | LD-1 | 10 | 210 |  |  | 0
FCU13-2 |  |  |  | 1230 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU13-3
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU13-3 (FCU-N) |  | Area: 1302
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | COOL | HEAT
Model Num | HPPR022W4R411R000 |  |  |  | SA CFM | 1640 |  | 10.4 GPM | 4.3 GPM
Serial Num |  |  |  |  | Fan Speed
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 120
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F133-1 | STUDY | SR | 8 |  |  |  | #DIV/0! | MISSING CFM
F133-2 | BED 2 | LD-1 | 8 | 185 |  |  | 0
F133-3 | BED 2 | LD-1 | 8 | 185 |  |  | 0
F133-4 | BED 1 | LD-1 | 8 | 190 |  |  | 0
F133-5 | BED 1 | LD-1 | 8 | 190 |  |  | 0
F133-6 | LIVING | LD-1 | 10 | 225 |  |  | 0
F133-7 | LIVING | LD-1 | 10 | 220 |  |  | 0
F133-8 | LIVING | LD-1 | 10 | 220 |  |  | 0
F133-9 | LIVING | LD-1 | 10 | 225 |  |  | 0
FCU13-3 |  |  |  | 1640 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU13-4
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU13-4 (FCU-CORR) |  | Area: 13004 CORRIDOR
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | COOL | HEAT
Model Num | HPPR008W4R321R000 |  |  |  | SA CFM | 494 |  | 2.2 GPM | 2.9 GPM
Serial Num |  |  |  |  | Fan Speed
[5 empty] | OA CFM |  |  | Return not ducted. 1/21/25
[5 empty] | RA CFM | 920
Motor Data |  |  |  |  | RL Voltage | 120
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F134-1 | CORR | LD | 8 | 123 |  |  | 0
F134-2 | CORR | LD | 8 | 124 |  |  | 0
F134-3 | CORR | LD | 8 | 123 |  |  | 0
F134-4 | CORR | LD | 8 | 124 |  |  | 0
FCU13-4 |  |  |  | 494 |  | 0 | 0
R134-1 | CORR | RR | 12X12 | 920 |  |  | 0
|  |  |  | 920 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU13-5
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU13-5 (FCU-O) |  | Area: 1303
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | COOL | HEAT
Model Num |  |  |  |  | SA CFM | 1810 |  | 10.4 GPM | 4.3 GPM
Serial Num |  |  |  |  | Fan Speed
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 120
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F135-1 | STUDY | SR | 8 | 160 |  |  | 0
F135-2 | BED 1 | LD-1 | 8 | 185 |  |  | 0
F135-3 | BED 1 | LD-1 | 8 | 185 |  |  | 0
F135-4 | BED 2 | LD-1 | 8 | 180 |  |  | 0
F135-5 | BED 2 | LD-1 | 8 | 180 |  |  | 0
F135-6 | LIVING | LD-1 | 10 | 230 |  |  | 0
F135-7 | LIVING | LD-1 | 10 | 230 |  |  | 0
F135-8 | LIVING | LD-1 | 10 | 230 |  |  | 0
F135-9 | LIVING | LD-1 | 10 | 230 |  |  | 0
FCU13-5 |  |  |  | 1810 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU13-6
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU13-6 (FCU-LOBBY) |  | Area: 1312 LOBBY
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | COOL | HEAT
Model Num | HPPR006W4R421R000 |  |  |  | SA CFM | 300 |  | 1.5 GPM | 1.8 GPM
Serial Num |  |  |  |  | Fan Speed
OA CFM
[5 empty] | RA CFM | 250 |  | Return not ducted. 1/21/25
Motor Data |  |  |  |  | RL Voltage | 120
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F136-1 | LOBBY | CD-8 | 8 | 200 |  |  | 0
F136-2 | 1313 | SR-Z |  | 50 |  |  | 0
F136-3 | 1314 | SR-ZA | 8 | 50 |  |  | 0
SUPPLY |  |  |  | 300 |  | 0 | 0
R136-1 | LOBBY | RR-9 |  | 200 |  |  | 0
R136-2 | 1313 | RR-Z |  | 50 |  |  | 0
RETURN |  |  |  | 250 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU13-7
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU13-7 (FCU-P-1) |  | Area: 1304
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | COOL | HEAT
Model Num | HPPR010W4R411R000 |  |  |  | SA CFM | 960 |  | 4.2 GPM | 2.1 GPM
Serial Num |  |  |  |  | Fan Speed
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 120
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 120 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F137-1 | STUDY | LD-1 | 8 | 160 |  |  | 0
F137-2 | STUDY | LD-1 | 8 | 160 |  |  | 0
F137-3 | BED 1 | LD-1 | 8 | 180 |  |  | 0
F137-4 | BED 2 | LD-1 | 8 | 155 |  |  | 0
F137-5 | BED 2 | LD-1 | 8 | 150 |  |  | 0
F137-6 | BED 2 | LD-1 | 8 | 155 |  |  | 0
FCU13-7 |  |  |  | 960 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU13-8
National TAB
Project: Formica Building (Cincinnati, OH)
Address: 120 E 4th Street Cincinnati, OH 45202
Asset: FCU13-8 (FCU-P-2) |  | Area: 1304
Unit Data |  |  |  |  | Test Data
MFG | WHALEN |  |  |  |  | Design | Actual | COOL | HEAT
Model Num | HPPR022W4R411R000 |  |  |  | SA CFM | 1890 | 1962 | 10.4 GPM | 4.3 GPM
Serial Num | 356687-15 |  |  |  | Fan Speed |  | MED
[5 empty] | OA CFM |  | 0
[5 empty] | RA CFM |  | 1962
Motor Data |  |  |  |  | RL Voltage | 120 | 124
Motor MFG | NL |  |  |  | RL Amperage |  | 7.9 | Unit filters clogged; removed for testing. Amperage is for both motors at the same time. Unit turned off after testing due to how clogged unit filter was. Note left on thermostat and disconnect stating to "replace filter prior to repowering.
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.24"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.23"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.47"
Voltage (rated) | 120 |  |  |  | Brake HP |  | 0.512
Amperage (rated) | 7.7
QTY |  | 2
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F138-1 | LIVING | LD-1 | 8 | 185 | 217 | 189 | 1.0216
F138-2 | LIVING | LD-1 | 8 | 185 | 212 | 184 | 0.99459
F138-3 | DINING | LD-1 | 8 | 190 | 219 | 196 | 1.0316
F138-4 | DINING | LD-1 | 8 | 190 | 215 | 192 | 1.0105
F138-5 | DINING | LD-1 | 8 | 190 | 225 | 202 | 1.0632
F138-6 | LIVING | LD-1 | 8 | 190 | 220 | 197 | 1.0368
F138-7 | LIVING | LD-1 | 8 | 190 | 213 | 190 | 1
F138-8 | LIVING | LD-1 | 8 | 190 | 231 | 208 | 1.0947
F138-9 | LIVING | LD-1 | 8 | 190 | 229 | 206 | 1.0842
F138-10 | LIVING | LD-1 | 8 | 190 | 210 | 198 | 1.0421
FCU13-8 |  |  |  | 1890 | 2191 | 1962 | 1.0381
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP