## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | KITCHE | 1400 | 1416 | 1150 | 1155 | 250 | 261 | 17.86% | 18.43%
AHU-2 | BOH | 1400 | 1360 | 1120 | 1059 | 280 | 301 | 20% | 22.13%
MUA-1 | COOKLINE | [8 empty] | 2160 | 2227
EF-1 | HD1 | [10 empty] | 2700 | 2621
EF-2 | RESTROOM | [12 empty] | 200 | 213
TOTALS |  | 2800 | 2776 | 2270 | 2214 | 530 | 562 |  |  | 2160 | 2227 | 2700 | 2621 | 200 | 213
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2690 | 2789 |  | FRONT |  | -0.0033 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2900 | 2834 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -210 | -45 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0033 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0