## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | Bar/Dining 1/RR | 6000 | 5781 | 4600 | 5781 | 1400 | 0 | 23.33% | 0%
RTU-2 | Dining 2 | 6000 | 5910 | 4600 | 5910 | 1400 | 0 | 23.33% | 0%
RTU-3 | Dining 3 | 4000 | 4174 | 3000 | 4174 | 1000 | 0 | 25% | 0%
RTU-4 | Office/Data Room/Kitchen | 4000 | 3684 | 3000 | 3684 | 1000 | 0 | 25% | 0%
RTU-5 | Kitchen/Storage/Lockers | 6000 | 5589 | 5000 | 5589 | 1000 | 0 | 16.67% | 0%
MUA-1 | Kitchen | [8 empty] | 7592 | 8112
EF-1 | Pizza Oven | [10 empty] | 1894 | 1846
EF-2 | Main Cookline (right) | [10 empty] | 3375 | 3407
EF-3 | Main Cookline (left) | [10 empty] | 1950 | 1948
EF-4 | Prep Cooking | [10 empty] | 1800 | 1740
EF-5 | S/S Condensate | [10 empty] | 1900 | 1895
EF-7 | Kitchen Vestibule | [10 empty] | 400 | 390
EF-6 | Public Restroom | [12 empty] | 510 | 517
TOTALS |  | 26000 | 25138 | 20200 | 25138 | 5800 | 0 |  |  | 7592 | 8112 | 11319 | 11226 | 510 | 517
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 13392 | 8112 |  | FRONT |  | -0.063 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 11829 | 11743 |  | SIDE |  | -0.058 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1563 | -3631 |  | REAR |  | -0.071 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.064 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0